## log_map
Room | Logged_variable_name | Comment | Log_variable_location | Has been moved from original location | Graph_name | Graph_location | Name in BMS system (location if not in the main page of the room/system) | Zone | Level | Logging interval [m] | Number of points in the log | Log period [days] | second sent in BMS
LAB01_QMV01 | Space_heating_LAB01_energy | District heating accumulated energy supplied for LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoE1_HeatV1
LAB01_QMV01 | Space_heating_LAB01_volume | District heating accumulated volume supplied for LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Volume
LAB01_QMV01 | Space_heating_LAB01_power | District heating power currently supplied to LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoPowerV1
LAB01_QMV01 | Space_heating_LAB01_flow | District heating flow currently supplied to LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Flow
LAB01_QMV01 | Space_heating_LAB01_supply_temperature | District heating supply temperature currently supplied to LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature1
LAB01_QMV01 | Space_heating_LAB01_return_temperature | District heating return temperature currently supplied from LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature2
LAB01_QMV01 | Space_heating_LAB01_operation_hours | District heating accumulated number of operation hours for LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoHourCount

## Main energy supplies
Name | Name in JSON file for the SATO platform | Name in BMS system | Variable description | Variable category | Unit
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_energy | nvoE1_HeatV1_Raw | District heating accumulated energy supplied for the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_volume | nvoV1_Volume_Raw | District heating accumulated volume supplied for the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_power | nvoPowerV1 | District heating power currently supplied to the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_flow | nvoV1_Flow | District heating flow currently supplied to the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_supply_temperature | nvoTemperature1 | District heating supply temperature currently supplied to the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_return_temperature | nvoTemperature2 | District heating return temperature currently supplied from the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_operation_hours | nvoHourCount | District heating accumulated number of operation hours for the whole building | District heating
HT00-1_EM01 | /TM023_0_20_1121/Modbus Com B/HT.00-1-EM01/PM710/Modbus Signals/EL_whole_building_power | Real Power, Total | Electrical power supplied to the whole building | Electrical
HT00-1_EM01 | /TM023_0_20_1121/Modbus Com B/HT.00-1-EM01/PM710/Modbus Signals/EL_whole_building_energy | Signed Real Energy, Consumption | Accumulated electrical energy supplied to the whole building | Electrical
BK01_KVM01 | /TM023_0_20_1128/Lon/Net/BK01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DCW_whole_building_volume | nvoV1_Volume_Raw | Domestic cold water accumulated volume supplied to the whole building | Domestic cold water
BK01_KVM01 | /TM023_0_20_1128/Lon/Net/BK01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DCW_whole_building_flow | nvoV1_Flow | Domestic cold water current flow supplied to the whole building | Domestic cold water
BK01_KVM01 | /TM023_0_20_1128/Lon/Net/BK01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DCW_whole_building_operation_hours | nvoHourCount | Domestic cold water accumulated number of operation hours for the whole building | Domestic cold water

## AHUs
Name | Name in JSON file for the SATO platform | Name in BMS system | Variable description | Variable category | Unit | Name in BMS system |  | Variable description | Variable category | Number in picture
KOMF01 | /TM023_0_23_1.125/ATV_control | ATV control/FE29 | Exhaust fan power | Fan | kW | KOMF01 | KOMF02 | - | - | -
KOMF01 | /TM023_0_23_1.125/KOMF01/Air_flow_KOMF01 | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h | Exhaust fan flow | Fan | m^3/h | ATV control/FE29 | ATV control/FE29 | Exhaust fan power | Fan | 1
KOMF01 | /TM023_0_23_1.125/KOMF01/Pressure_diff_fan | SXW_VEN_Rotorveksler_000K/PDU01 | Exhaust fan pressure difference | Fan | Pa | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h | Exhaust fan flow | Fan | 2
KOMF01 | /TM023_0_23_1.125/KOMF01/Exhaust_fan_start | VU01_K | Exhaust fan on/off signal | Fan | Boolean | SXW_VEN_Rotorveksler_000K/PDU01 | SXW_VEN_Rotorveksler_000K/PDU01 | Exhaust fan pressure difference | Fan | 3
KOMF01 | /TM023_0_23_1.125/KOMF01/Alarm_filter_exhaust | PFU01_F | Extraction filter pressure | Alarm | Boolean | VU01_K | VU01_K | Exhaust fan on/off signal | Fan | 4
KOMF01 | /TM023_0_23_1.125/KOMF01/Alarm_intake_filter | PFU01_F | Intake filter pressure | Alarm | Boolean | PFU01_F | PFU01_F | Extraction filter pressure | Alarm | 5
KOMF01 | /TM023_0_23_1.125/KOMF01/ATV_control_supply | ATV control/FE29 | Supply fan power | Fan | kW | PFU01_F | PFI01_F | Intake filter pressure | Alarm | 6
KOMF01 | /TM023_0_23_1.125/KOMF01/Air_flow_supply | VI01_FLOW_m3_h | Supply fan flow | Fan | m^3/h | ATV control/FE29 | ATV control/FE29 | Supply fan power | Fan | 7
KOMF01 | /TM023_0_23_1.125/KOMF01/Air pressure_diff_supply | PDI01 | Supply fan pressure difference | Fan | Pa | VI01_FLOW_m3_h | VI01_FLOW_m3_h | Supply fan flow | Fan | 8
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_fan_start | VI01_K | Supply fan on/off signal | Fan | Boolean | PDI01 | PDI01 | Supply fan pressure difference | Fan | 9
KOMF01 | /TM023_0_23_1.125/KOMF01/Cooling_recovery_active_if | KØLIG_DIFF_T_AKT_SV (settings) | Activation criteria for cooling recovery: external air temperature minus extraction air temperature above threshold | Settings | °C | VI01_K | VI01_K | Supply fan on/off signal | Fan | 10
KOMF01 | /TM023_0_23_1.125/KOMF01/Cooling_recovery_inactive_if | KØLIG_DIFF_T_DEAKT_SV (settings) | Deactivation criteria for cooling recovery: extration air temperature minus external air temperature above threshold | Settings | °C | KØLIG_DIFF_T_AKT_SV (settings) | KØLG_DIFF_T_AKT_SV | Activation criteria for cooling recovery: external air temperature minus extraction air temperature above threshold | Settings | 11
KOMF01 | /TM023_0_23_1.125/KOMF01/Exhaust_fan_signal | VU01_S | Exhaust fan control signal | Fan | % | KØLIG_DIFF_T_DEAKT_SV (settings) | KØLG_DIFF_T_DEAKT_SV | Deactivation criteria for cooling recovery: extration air temperature minus external air temperature above threshold | Settings | 12
KOMF01 | /TM023_0_23_1.125/KOMF01/Exhaust_temperature | TU02 | Exhaust air temperature | Air temperature sensor | °C | VU01_S | VU01_S | Exhaust fan control signal | Fan | 13
KOMF01 | /TM023_0_23_1.125/KOMF01/Extraction_damper_on-off | SMU01_K | Extraction damper on/off signal | Damper | Boolean | TU02 | TU02 | Exhaust air temperature | Air temperature sensor | 14
KOMF01 | /TM023_0_23_1.125/KOMF01/Extraction_pressure | PTU01 | Extraction air pressure | Air pressure sensor | Pa | SMU01_K | SMU01_K | Extraction damper on/off signal | Damper | 15
KOMF01 | /TM023_0_23_1.125/KOMF01/Extraction_pressure_set-point | PTU01_SV (settings) | Extraction air pressure setpoint | Setpoint | Pa | PTU01 | PTU01 | Extraction air pressure | Air pressure sensor | 16
KOMF01 | /TM023_0_23_1.125/KOMF01/Extraction_temperature | TU01 | Extraction air temperature | Air temperature sensor | °C | PTU01_SV (settings) | PTU01_SV | Extraction air pressure setpoint | Setpoint | 17
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_control_valve | MVV01_S | Heating coil motorvalve position | Heating coil | % | TU01 | TU01 | Extraction air temperature | Air temperature sensor | 18
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_effect | power_f (energymeter) | Heating coil district heating current power output | Heating coil | W | MVV01_S | MVV01_S | Heating coil motorvalve position | Heating coil | 19
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_energy_accumulated | elec_whr_f (energymeter) | Heating coil district heating accumulated energy use | Heating coil | Wh | power_f (energymeter) | nvoPowerV1 | Heating coil district heating current power output | Heating coil | 20
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_flow | flow_f (energymeter) | Heating coil district heating current flow | Heating coil | l/s | elec_whr_f (energymeter) | nvoE1_HeatV1 | Heating coil district heating accumulated energy use | Heating coil | 21
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_operation_hours_accumulated | count_f (energymeter) | Heating coil time in operation | Heating coil | h | flow_f (energymeter) | nvoV1_Flow | Heating coil district heating current flow | Heating coil | 22
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_pump_on-off | PV01_K | Heating coil pump on/off signal | Heating coil | Boolean | count_f (energymeter) | nvoHourCount | Heating coil time in operation | Heating coil | 23
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_return_temperature | TR01 | Heating coil return water temperature | Heating coil | °C | PV01_K | PV01_K | Heating coil pump on/off signal | Heating coil | 24
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_return_temperature_DH | temp_p (energymeter) | Heating coil district heating return water temperature | Heating coil | °C | TR01 | TR01 | Heating coil return water temperature | Heating coil | 25
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_return_temperature_min_limit | TR01_SV (settings) | Heating coil lowest return water temperature allowed | Heating coil | °C | temp_p (energymeter) | nvoTemperature2 | Heating coil district heating return water temperature | Heating coil | 26
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_supply_temperature | TF01 | Heating coil supply water temperature | Heating coil | °C | TR01_SV (settings) | TR01_SV | Heating coil lowest return water temperature allowed | Heating coil | 27
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_supply_temperature_DH | temp_p (energymeter) | Heating coil district heating supply water temperature | Heating coil | °C | TF01 | TF01 | Heating coil supply water temperature | Heating coil | 28
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_volume_accumulated | vol_f (energymeter) | Heating coil district heating accumulated volume flow | Heating coil | l | temp_p (energymeter) | nvoTemperature1 | Heating coil district heating supply water temperature | Heating coil | 29
KOMF01 | /TM023_0_23_1.125/KOMF01/HE_efficiency | VIRKNINGSGRAD | Heat recovery efficiency | Rotary heat exchanger | % | vol_f (energymeter) | nvoV1_Volume | Heating coil district heating accumulated volume flow | Heating coil | 30
KOMF01 | /TM023_0_23_1.125/KOMF01/HE_signal | RV01_S | Rotation speed | Rotary heat exchanger | % | VIRKNINGSGRAD | VIRKNINGSGRAD | Heat recovery efficiency | Rotary heat exchanger | 31
KOMF01 | /TM023_0_23_1.125/KOMF01/Intake_damper_on-off | SMI01_K | Intake damper on/off signal | Damper | Boolean | RV01_S | RV01_S | Rotation speed | Rotary heat exchanger | 32
KOMF01 | /TM023_0_23_1.125/KOMF01/Intake_temperature | TI03 | Intake air temperature | Air temperature sensor | °C | SMI01_K | SMI01_K | Intake damper on/off signal | Damper | 33
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_cooling_active_if_diff_external_temperature_and_room_temperature_above | NATKØL_SV_D_TUD_TRU (settings) | Activation criteria for night cooling: room temperature minus external air temperature above threshold | Settings | °C | TI03 | TI03 | Intake air temperature | Air temperature sensor | 34
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_cooling_active_if_external_temperature_above | NATKØL_SV_LAV_TUD01 (settings) | Activation criteria for night cooling: external air temperature above threshold | Settings | °C | NATKØL_SV_D_TUD_TRU (settings) | NATKØL_SV_D_TUD_TRU | Activation criteria for night cooling: room temperature minus external air temperature above threshold | Settings | 35
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_cooling_active_if_room_temperature_above | NATKØL_SV_TRU01 (settings) | Activation criteria for night cooling: room temperature above threshold | Settings | °C | NATKØL_SV_LAV_TUD01 (settings) | NATKØL_SV_LAV_TUD01 | Activation criteria for night cooling: external air temperature above threshold | Settings | 36
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_cooling_max_operation_hours_per_day | NATKØL_SV_TIM_START (settings) | Maximum hours night cooling can be activated in one night | Settings | h | NATKØL_SV_TRU01 (settings) | NATKØL_SV_TRU01 | Activation criteria for night cooling: room temperature above threshold | Settings | 37
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_heating_active_if_room_temperature_below | NATVARME_SV_TRU01 (settings) | Activation cireteria for night heating: room temperature below threshold | Settings | °C | NATKØL_SV_TIM_START (settings) | NATKØL_SV_TIM_START | Maximum hours night cooling can be activated in one night | Settings | 38
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_heating_max_operation_hours_per_day | NATVAR_SV_TIM_START (settings) | Maximum hours night heating can be activated in one night | Settings | h | NATVARME_SV_TRU01 (settings) | NATVARME_SV_TRU01 | Activation cireteria for night heating: room temperature below threshold | Settings | 39
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_fan_signal | VI01_S | Supply fan control signal | Fan | % | NATVAR_SV_TIM_START (settings) | NATVAR_SV_TIM_START | Maximum hours night heating can be activated in one night | Settings | 40
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_pressure | PTI01 | Supply air pressure | Air pressure sensor | Pa | VI01_S | VI01_S | Supply fan control signal | Fan | 41
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_pressure_set-point | PTI01_SV (settings) | Supply air pressure setpoint | Setpoint | Pa | PTI01 | PTI01 | Supply air pressure | Air pressure sensor | 42
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature | TI01 | Supply air temperature | Air temperature sensor | °C | PTI01_SV (settings) | PTI01_SV | Supply air pressure setpoint | Setpoint | 43
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X | TI01_KURVE_X (settings) | External air temperature (should be the same for both AHUs) | Air temperature sensor | °C | TI01 | TI01 | Supply air temperature | Air temperature sensor | 44
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X1 | TI01_KURVE_X1 (settings) | - | Settings | °C | TI01_KURVE_X (settings) | - | External air temperature (should be the same for both AHUs) | Air temperature sensor | 45
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X2 | TI01_KURVE_X2 (settings) | - | Settings | °C | TI01_KURVE_X1 (settings) | - | - | Settings | 46
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X3 | TI01_KURVE_X3 (settings) | - | Settings | °C | TI01_KURVE_X2 (settings) | - | - | Settings | 47
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_Y | TI01_KURVE (settings) | - | Settings | °C | TI01_KURVE_X3 (settings) | - | - | Settings | 48
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_Y1 | TI01_KURVE_Y1 (settings) | - | Settings | °C | TI01_KURVE (settings) | - | - | Settings | 49
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_Y2 | TI01_KURVE_Y2 (settings) | - | Settings | °C | TI01_KURVE_Y1 (settings) | - | - | Settings | 50
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_Y3 | TI01_KURVE_Y3 (settings) | - | Settings | °C | TI01_KURVE_Y2 (settings) | - | - | Settings | 51
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_set-point | TI01_KALK_SV | Supply air temperature setpoint | Setpoint | °C | TI01_KURVE_Y3 (settings) | - | - | Settings | 52
KOMF01 | /TM023_0_23_1.125/KOMF01/Temperature_after_HE_before_HC | TI02 | Air temperature after HE | Air temperature sensor | °C | TI01_KALK_SV | TI01_KALK_SV | Supply air temperature setpoint | Setpoint | 53
KOMF01 | /TM023_0_23_1.125/KOMF01/Winter_mode_active_if_external_temperature_below | TI01_REG_SV_LAV_UT (settings) | Activation criteria for winter mode: external air temperature below threshold | Settings | °C | TI02 | TI02 | Air temperature after HE | Air temperature sensor | 54
KOMF01 | /TM023_0_23_1.125/KOMF01/ventilation_system_status | VEN_STATUS | AHU status | Overall | Status code | TI01_REG_SV_LAV_UT (settings) | TI01_REG__SV_LAV_UT | Activation criteria for winter mode: external air temperature below threshold | Settings | 55
KOMF01 | /TM023_0_23_1.125/IO Bus/M3_UI-16/Heat_coil_alarm | TFI01 | Heating coil temperature | Alarm | Boolean | VEN_STATUS | VEN_STATUS | AHU status | Overall | 56
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_Extended_run_time_ventilation_system | DT01_FORL_DR_TID_SV | Manual override for extending the running time of the ahu | Settings | min | TFI01 | TFI01 | Heating coil temperature | Alarm | 57
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_status_extended_run_time | DT01_FORL_DRIFT | Status of the manual override for extending the running time of the AHU | Settings | Boolean | DT01_FORL_DR_TID_SV | DT01_FORL_DR_TID_SV | Manual override for extending the running time of the ahu | Settings | 58
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_supply_temperature | TI01_SV | - | Settings | °C | DT01_FORL_DRIFT | DT01_FORL_DRIFT | Status of the manual override for extending the running time of the AHU | Settings | 59
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_desired_room_temperature | TRU01_SV | - | Settings | °C | TI01_SV | TI01_SV | - | Settings | 60
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_max_inlet_temp | TI01_KALK_TRU_MAX_SV | - | Settings | °C | TRU01_SV | TRU01_SV | - | Settings | 61
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_min_inlet_temp | TI01_KALK_TRU_MIN_SV | - | Settings | °C | TI01_KALK_TRU_MAX_SV | TI01_KALK_TRU_MAX_SV | - | Settings | 62
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_desired_outlet_temp | TU01_SV | - | Settings | °C | TI01_KALK_TRU_MIN_SV | TI01_KALK_TRU_MIN_SV | - | Settings | 63
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_max_outlet_temp | TI01_KALK_TU_MAX_SV | - | Settings | °C | TU01_SV | TU01_SV | - | Settings | 64
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_min_outlet_temp | TI01_KALK_TU_MIN_SV | - | Settings | °C | TI01_KALK_TU_MAX_SV | TI01_KALK_TU_MAX_SV | - | Settings | 65
KOMF01 | /TM023_0_23_1.125/KOMF01/Temperature_room_1.136 | 1136_TRU01 | Reference room temperature | Overall | °C | TI01_KALK_TU_MIN_SV | TI01_KALK_TU_MIN_SV | - | Settings | 66
KOMF01 | /TM023_0_23_1.125/KOMF01/Temperature_room_1.255 | 1255_TRU01 | Reference room temperature | Overall | °C | 1136_TRU01 | 1104_TRU01 | Reference room temperature | Overall | 67
KOMF01 | /TM023_0_23_1.125/KOMF01/Temperature_room_1.365 | 1365_TRU01 | Reference room temperature | Overall | °C | 1255_TRU01 | 1218_TRU01 | Reference room temperature | Overall | 68
KOMF01 | /TM023_0_23_1.125/KOMF01/SEL_value | SEL_VÆRDI_J_m3 | SEL value | Fan | J/m^3 | 1365_TRU01 | 1316_TRU01 | Reference room temperature | Overall | 69
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/EnergyMeas [1]/nvoPartialkWh Log | elec_kwh_l | Total electricity use of AHU | Overall | kWh | SEL_VÆRDI_J_m3 | SEL_VÆRDI_J_m3 | SEL value | Fan | 70
KOMF02 | /TM023_0_20_1.011/ModbusA VEXX/ATV212 KOMF02 VU01/ATV_power_exhaust | ATV control/FE29 | Exhaust fan power | Fan | kW | elec_kwh_l | elec_kwh_l | Total electricity use of AHU | Overall | 71
KOMF02 | /TM023_0_20_1.011/KOMF02/Exhaust_flow | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h | Exhaust fan flow | Fan | m^3/h
KOMF02 | /TM023_0_20_1.011/KOMF02/Pressure_diff_fan | SXW_VEN_Rotorveksler_000K/PDU01 | Exhaust fan pressure difference | Fan | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Fan_exhaust_status | VU01_K | Exhaust fan on/off signal | Fan | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Alarm_filter_exhaust | PFU01_F | Extraction filter pressure | Alarm | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Alarm_filter_intake | PFI01_F | Intake filter pressure | Alarm | Boolean
KOMF02 | /TM023_0_20_1.011/ModbusA VEXX/ATV212 KOMF02 VI01/ATV_power_supply | ATV control/FE29 | Supply fan power | Fan | kW
KOMF02 | /TM023_0_20_1.011/KOMF02/Air_flow_supply | VI01_FLOW_m3_h | Supply fan flow | Fan | m^3/h
KOMF02 | /TM023_0_20_1.011/KOMF02/Pressure_diff_fan_supply | PDI01 | Supply fan pressure difference | Fan | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Fan_intake_status | VI01_K | Supply fan on/off signal | Fan | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_cooling_recovery_active_setpoint | KØLG_DIFF_T_AKT_SV | Activation criteria for cooling recovery: external air temperature minus extraction air temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_cooling_recovery_inactive_setpoint | KØLG_DIFF_T_DEAKT_SV | Deactivation criteria for cooling recovery: extration air temperature minus external air temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Fan_exhaust_speed | VU01_S | Exhaust fan control signal | Fan | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_exhaust_after_heatexchange | TU02 | Exhaust air temperature | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Damper_exhaust | SMU01_K | Extraction damper on/off signal | Damper | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Exhaust_pressure | PTU01 | Extraction air pressure | Air pressure sensor | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_outlet_pressure | PTU01_SV | Extraction air pressure setpoint | Setpoint | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_exhaust | TU01 | Extraction air temperature | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Motor_valve_heat_coil | MVV01_S | Heating coil motorvalve position | Heating coil | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Energy_heat_coil | nvoPowerV1 | Heating coil district heating current power output | Heating coil | W
KOMF02 | /TM023_0_20_1.011/KOMF02/Total_energy_heat_coil | nvoE1_HeatV1 | Heating coil district heating accumulated energy use | Heating coil | Wh
KOMF02 | /TM023_0_20_1.011/KOMF02/Flow_heat_coil | nvoV1_Flow | Heating coil district heating current flow | Heating coil | l/s
KOMF02 | /TM023_0_20_1.011/KOMF02/Hour_counter_heating_coil | nvoHourCount | Heating coil time in operation | Heating coil | h
KOMF02 | /TM023_0_20_1.011/KOMF02/Heat_coil_pump | PV01_K | Heating coil pump on/off signal | Heating coil | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_return_heat_coil | TR01 | Heating coil return water temperature | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Return_temp_heat_coil | nvoTemperature2 | Heating coil district heating return water temperature | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_min_return_temp_heating_coil | TR01_SV | Heating coil lowest return water temperature allowed | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_supply_heat_coil | TF01 | Heating coil supply water temperature | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Supply_temp_heat_coil | nvoTemperature1 | Heating coil district heating supply water temperature | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Total_volume_heat_coil | nvoV1_Volume | Heating coil district heating accumulated volume flow | Heating coil | l
KOMF02 | /TM023_0_20_1.011/KOMF02/Heat_exchanger_efficiency | VIRKNINGSGRAD | Heat recovery efficiency | Rotary heat exchanger | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Heat_exchanger_speed | RV01_S | Rotation speed | Rotary heat exchanger | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Damper_intake | SMI01_K | Intake damper on/off signal | Damper | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_intake | TI03 | Intake air temperature | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_night_cooling_when_outdoor_temp_below_room_temp | NATKØL_SV_D_TUD_TRU | Activation criteria for night cooling: room temperature minus external air temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_night_cooling_room_temp_outdoor_temp | NATKØL_SV_LAV_TUD01 | Activation criteria for night cooling: external air temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_night_cooling_room_temp | NATKØL_SV_TRU01 | Activation criteria for night cooling: room temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_max_time_night_cooling | NATKØL_SV_TIM_START | Maximum hours night cooling can be activated in one night | Settings | h
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_night_heating | NATVARME_SV_TRU01 | Activation cireteria for night heating: room temperature below threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_max_time_night_heating | NATVAR_SV_TIM_START | Maximum hours night heating can be activated in one night | Settings | h
KOMF02 | /TM023_0_20_1.011/KOMF02/Fan_intake_speed | VI01_S | Supply fan control signal | Fan | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Intake_pressure | PTI01 | Supply air pressure | Air pressure sensor | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_inlet_pressure | PTI01_SV | Supply air pressure setpoint | Setpoint | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_inlet | TI01 | Supply air temperature | Air temperature sensor | °C
KOMF02 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X | TI01_KURVE_X (settings) | External air temperature (should be the same for both AHUs) | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_setpoint_inlet | TI01_KALK_SV | Supply air temperature setpoint | Setpoint | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_before_heat_coil | TI02 | Air temperature after HE | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_winther_start_up_temp | TI01_REG__SV_LAV_UT | Activation criteria for winter mode: external air temperature below threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/ventilation_system_status | VEN_STATUS | AHU status | Overall | Status code
KOMF02 | /TM023_0_20_1.011/KOMF02/Heat_coil_alarm | TFI01 | Heating coil temperature | Alarm | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_Extended_run_time_ventilation_system | DT01_FORL_DR_TID_SV | Manual override for extending the running time of the ahu | Settings | min
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_status_extended_run_time | DT01_FORL_DRIFT | Status of the manual override for extending the running time of the AHU | Settings | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_supply_temperature | TI01_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_desired_room_temperature | TRU01_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_max_inlet_temp | TI01_KALK_TRU_MAX_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_min_inlet_temp | TI01_KALK_TRU_MIN_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_desired_outlet_temp | TU01_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_max_outlet_temp | TI01_KALK_TU_MAX_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_min_outlet_temp | TI01_KALK_TU_MIN_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temperature_room_1.104 | 1104_TRU01 | Reference room temperature | Overall | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temperature_room_1.218 | 1218_TRU01 | Reference room temperature | Overall | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temperature_room_1.316 | 1316_TRU01 | Reference room temperature | Overall | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/SEL_value | SEL_VÆRDI_J_m3 | SEL value | Fan | J/m^3
KOMF02 | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/EnergyMeas [1]/nvoPartialkWh Log | elec_kwh_l | Total electricity use of AHU | Overall | kWh
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45 - 52
53
54
55
56
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71

## Rooms
Name | Name in JSON file for the SATO platform | Name in BMS system | Variable description | Variable category | Unit | Variable category | Variable | Unit | Included? | Variable description | Number in picture
R.1.132 | /TM023_2_20_1.103B/Damper_position_1.132 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | % | CO2 | CO201 | ppm | X | Current measured CO2 level in the room | 1
R.1.132 | /TM023_2_20_1.103B/Lux_meter_1.132 | LUX01 | Light level measured in the ceiling | Light | Lux | CO2 | CO201_SV | ppm | X | Current upper limit setpoint for the CO2 level | 2
R.1.132 | /TM023_2_20_1.103B/Light_ON_OFF_1.132 | LY01 | ON/OFF of the light | Light | Boolean | Light | EK10 | Boolean | X | ON/OFF switch due to high lux level in the room measured in the ceiling | 3
R.1.132 | /TM023_2_20_1.103B/Light_level_1.132 | LN01 | Light level setpoint | Light | % | Light | LN01 | % | X | Light level setpoint | 4
R.1.132 | /TM023_2_20_1.103B/PIR_Activity_1.132 | ZoneAktiv | If the room is considered active | Occupancy | Boolean | Light | LN02 | % | (X) | Additional light level setpoint (only relevant for some rooms)
R.1.132 | /TM023_2_20_1.103B/Room_temperature_1.132 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C | Light | LUX01 | Lux | X | Light level measured in the ceiling | 5
R.1.132 | /TM023_2_20_1.103B/CO2_level_1.132 | CO201 | Current measured CO2 level in the room | CO2 | ppm | Light | LUX01Setpunkt | Lux | X | Light level setpoint for when to switch off the light | 6
R.1.132 | /TM023_2_20_1.103B/Window_position_1.132 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean | Light | LY01 | Boolean | X | ON/OFF of the light | 7
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/CO2_setpoint_1.132 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm | Light | LY02 | Boolean | (X) | Additional ON/OFF of the light (only relevant for some rooms)
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Light_off_switch_high_lux_1.132 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean | Light | LYS_STR350_man | Boolean | X | Manual ON/OFF switch for the light located in the room control panel | 8
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Lux_level_setpoint_1.132 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux | Occupancy | PIR01DelayOff | s | X | Delay between the room being active and when the light is turned off automatically | 9
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Manual_light_on_off_switch_1.132 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean | Occupancy | PIR01 | Boolean | X | Measurement from the PIR sensor to determine if occupied or not | 10
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Light_automatic_off_delay_1.132 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s | Occupancy | ZoneAktiv | Boolean | X | If the room is considered active | 11
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/PIR_1.132 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean | Ventilation | SMIU01 | Boolean | (X) | ON/OFF signal for the supply/extraction damper in CAV supplied rooms | 12
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Ventilation_off_delay_1.132 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s | Ventilation | VAV01_02 | % | (X) | Position of the supply/extraction damper in VAV supplied rooms | 12
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Ventilation_AHU_status_1.132 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code | Ventilation | VentForsStop | s | X | Delay between the room being active and when the ventilation dampers are closed automatically | 13
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Heating_valve_1.132 | TA01 | Opening signal of the radiator valve | Heating | % | Ventilation | VentStatus | Status code | X | Status of the AHU supplying the room | 14
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Temperature_offset_from_global_1.132 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C | Window | VINDUE_ÅBEN | Boolean | X | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | 15
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Temperature_cooling_setpoint_1.132 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C | Heating | TA01 | % | X | Opening signal of the radiator valve | 16
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Temperature_heating_setpoint_1.132 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C | Temperature | TRU01 | °C | X | Measured room temperature (cannot be assumed to be either air or operative temperature) | 17
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Temperature_global_setpoint_1.132 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C | Temperature | TRU01_OffSet | °C | X | Offset from the global temperature setpoint (manually set by the user) | 18
R.1.136 | /TM023_2_20_1.103B/Damper_position_1.136 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | % | Temperature | TRU01DødZoneDag | °C | (X) | Deadband during daytime | 19
R.1.136 | /TM023_2_20_1.103B/Lux_meter_1.136 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean | Temperature | TRU01DødZoneNat | °C | (X) | Deadband during nighttime | 20
R.1.136 | /TM023_2_20_1.103B/Light_ON_OFF_1.136 | LY01 | ON/OFF of the light | Light | Boolean | Temperature | TRU01DødZoneStandby | °C | (X) | Deadband during standby | 21
R.1.136 | /TM023_2_20_1.103B/Light_level_1.136 | LN01 | Light level setpoint | Light | % | Temperature | TRU01KalkKøl | °C | X | Upper limit for activating cooling | 22
R.1.136 | /TM023_2_20_1.103B/Light_level_blackboard | LN02 | Additional light level setpoint (only relevant for some rooms) | Light | % | Temperature | TRU01KalkVarme | °C | X | Lower limit for activating heating | 23
R.1.136 | /TM023_2_20_1.103B/Light_ON_OFF_blackboard | LY02 | Additional ON/OFF of the light (only relevant for some rooms) | Light | Boolean | Temperature | TRU01SetVærdi | °C | X | Global temperature setpoint | 24
R.1.136 | /TM023_2_20_1.103B/PIR_activity_1.136 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.136 | /TM023_2_20_1.103B/Room_temperature_1.136 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.136 | /TM023_2_20_1.103B/CO2_1.136 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.136 | /TM023_2_20_1.103B/window_position_1.136 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/CO2_setpoint_1.136 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Light_off_switch_high_lux_1.136 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Lux_level_setpoint_1.136 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Manual_light_on_off_switch_1.136 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Light_automatic_off_delay_1.136 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Lux_level_ceiling_1.136 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Ventilation_off_delay_1.136 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Ventilation_AHU_status_1.136 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Heating_valve_1.136 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Temperature_offset_from_global_1.136 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Temperature_cooling_setpoint_1.136 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Temperature_heating_setpoint_1.136 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Temperature_global_setpoint_1.136 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.248 | /TM023_3_21_1.204/Damper_position_1.248 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.248 | /TM023_3_21_1.204/Lux_meter_1.248 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.248 | /TM023_3_21_1.204/Light_ON_OFF_1.248 | LY01 | ON/OFF of the light | Light | Boolean
R.1.248 | /TM023_3_21_1.204/Light_level_1.248 | LN01 | Light level setpoint | Light | %
R.1.248 | /TM023_3_21_1.204/PIR_activity_1.248 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.248 | /TM023_3_21_1.204/Room_temperature_1.248 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.248 | /TM023_3_21_1.204/CO2_level_1.248 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.248 | /TM023_3_21_1.204/Window_position_1.248 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/CO2_setpoint_1.248 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Light_off_switch_high_lux_1.248 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Lux_level_ceiling_1.248 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Lux_level_setpoint_1.248 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Manual_light_on_off_switch_1.248 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Light_automatic_off_delay_1.248 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Ventilation_off_delay_1.248 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.248 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Heating_valve_1.248 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Temperature_offset_from_global_1.248 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Temperature_cooling_setpoint_1.248 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Temperature_heating_setpoint_1.248 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Temperature_global_setpoint_1.248 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.250 | /TM023_3_21_1.204/Damper_position_1.250 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.250 | /TM023_3_21_1.204/Lux_meter_1.250 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.250 | /TM023_3_21_1.204/Light_ON_OFF_1.250 | LY01 | ON/OFF of the light | Light | Boolean
R.1.250 | /TM023_3_21_1.204/Light_level_1.250 | LN01 | Light level setpoint | Light | %
R.1.250 | /TM023_3_21_1.204/PIR_activity_1.250 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.250 | /TM023_3_21_1.204/Room_temperature_1.250 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.250 | /TM023_3_21_1.204/CO2_level_1.250 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.250 | /TM023_3_21_1.204/Window_position_1.250 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/CO2_setpoint_1.250 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Light_off_switch_high_lux_1.250 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Lux_level_ceiling_1.250 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Lux_level_setpoint_1.250 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Manual_light_on_off_switch_1.250 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Light_automatic_off_delay_1.250 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Ventilation_off_delay_1.250 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.250 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Heating_valve_1.250 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Temperature_offset_from_global_1.250 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Temperature_cooling_setpoint_1.250 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Temperature_heating_setpoint_1.250 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Temperature_global_setpoint_1.250 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.252 | /TM023_3_21_1.204/Damper_position_1.252 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.252 | /TM023_3_21_1.204/Lux_meter_1.252 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.252 | /TM023_3_21_1.204/Light_ON_OFF_1.252 | LY01 | ON/OFF of the light | Light | Boolean
R.1.252 | /TM023_3_21_1.204/Light_level_1.252 | LN01 | Light level setpoint | Light | %
R.1.252 | /TM023_3_21_1.204/PIR_activity_1.252 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.252 | /TM023_3_21_1.204/Room_temperature_1.252 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.252 | /TM023_3_21_1.204/CO2_level_1.252 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.252 | /TM023_3_21_1.204/Window_position_1.252 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/CO2_setpoint_1.252 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Light_off_switch_high_lux_1.252 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Lux_level_ceiling_1.252 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Lux_level_setpoint_1.252 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Manual_light_on_off_switch_1.252 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Light_automatic_off_delay_1.252 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Ventilation_off_delay_1.252 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.252 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Heating_valve_1.252 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Temperature_offset_from_global_1.252 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Temperature_cooling_setpoint_1.252 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Temperature_heating_setpoint_1.252 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Temperature_global_setpoint_1.252 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.253 | /TM023_3_21_1.204/Damper_position_1.253 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.253 | /TM023_3_21_1.204/Lux_meter_1.253 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.253 | /TM023_3_21_1.204/Light_ON_OFF_1.253 | LY01 | ON/OFF of the light | Light | Boolean
R.1.253 | /TM023_3_21_1.204/Light_level_1.253 | LN01 | Light level setpoint | Light | %
R.1.253 | /TM023_3_21_1.204/PIR_activity_1.253 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.253 | /TM023_3_21_1.204/Room_temperature_1.253 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.253 | /TM023_3_21_1.204/CO2_level_1.253 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.253 | /TM023_3_21_1.204/Window_position_1.253 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/CO2_setpoint_1.253 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Light_off_switch_high_lux_1.253 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Lux_level_setpoint_1.253 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Manual_light_on_off_switch_1.253 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Light_automatic_off_delay_1.253 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/PIR_1.253 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Ventilation_off_delay_1.253 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.253 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Heating_valve_1.253 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Temperature_offset_from_global_1.253 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Temperature_cooling_setpoint_1.253 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Temperature_heating_setpoint_1.253 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Temperature_global_setpoint_1.253 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.255 | /TM023_3_21_1.204/Damper_position_1.255 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.255 | /TM023_3_21_1.204/Lux_meter_1.255 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.255 | /TM023_3_21_1.204/Light_ON_OFF_1.255 | LY01 | ON/OFF of the light | Light | Boolean
R.1.255 | /TM023_3_21_1.204/Light_level_1.255 | LN01 | Light level setpoint | Light | %
R.1.255 | /TM023_3_21_1.204/PIR_activity_1.255 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.255 | /TM023_3_21_1.204/Room_temperature_1.255 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.255 | /TM023_3_21_1.204/CO2_level_1.255 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.255 | /TM023_3_21_1.204/Window_position_1.255 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/CO2_setpoint_1.255 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Light_off_switch_high_lux_1.255 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Lux_level_ceiling_1.255 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Lux_level_setpoint_1.255 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Manual_light_on_off_switch_1.255 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Light_automatic_off_delay_1.255 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Ventilation_off_delay_1.255 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.255 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Heating_valve_1.255 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Temperature_offset_from_global_1.255 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Temperature_cooling_setpoint_1.255 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Temperature_heating_setpoint_1.255 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Temperature_global_setpoint_1.255 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.256 | /TM023_3_21_1.204/Damper_position_1.256 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.256 | /TM023_3_21_1.204/Lux_meter_1.256 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.256 | /TM023_3_21_1.204/Light_ON_OFF_1.256 | LY01 | ON/OFF of the light | Light | Boolean
R.1.256 | /TM023_3_21_1.204/Light_level_1.256 | LN01 | Light level setpoint | Light | %
R.1.256 | /TM023_3_21_1.204/PIR_activity_1.256 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.256 | /TM023_3_21_1.204/Room_temperature_1.256 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.256 | /TM023_3_21_1.204/CO2_level_1.256 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.256 | /TM023_3_21_1.204/Window_position_1.256 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/CO2_setpoint_1.256 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Light_off_switch_high_lux_1.256 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Lux_level_ceiling_1.256 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Lux_level_setpoint_1.256 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Manual_light_on_off_switch_1.256 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Light_automatic_off_delay_1.256 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Ventilation_off_delay_1.256 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.256 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Heating_valve_1.256 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Temperature_offset_from_global_1.256 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Temperature_cooling_setpoint_1.256 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Temperature_heating_setpoint_1.256 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Temperature_global_setpoint_1.256 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.257 | /TM023_3_21_1.204/Damper_position_1.257 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.257 | /TM023_3_21_1.204/Lux_meter_1.257 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.257 | /TM023_3_21_1.204/Light_ON_OFF_1.257 | LY01 | ON/OFF of the light | Light | Boolean
R.1.257 | /TM023_3_21_1.204/Light_level_1.257 | LN01 | Light level setpoint | Light | %
R.1.257 | /TM023_3_21_1.204/PIR_activity_1.257 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.257 | /TM023_3_21_1.204/Room_temperature_1.257 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.257 | /TM023_3_21_1.204/CO2_level_1.257 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.257 | /TM023_3_21_1.204/Window_position_1.257 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/CO2_setpoint_1.257 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Light_off_switch_high_lux_1.257 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Lux_level_ceiling_1.257 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Lux_level_setpoint_1.257 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Manual_light_on_off_switch_1.257 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Light_automatic_off_delay_1.257 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Ventilation_off_delay_1.257 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.257 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Heating_valve_1.257 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Temperature_offset_from_global_1.257 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Temperature_cooling_setpoint_1.257 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Temperature_heating_setpoint_1.257 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Temperature_global_setpoint_1.257 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.258 | /TM023_3_21_1.204/Damper_position_1.258 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.258 | /TM023_3_21_1.204/Lux_meter_1.258 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.258 | /TM023_3_21_1.204/Light_ON_OFF_1.258 | LY01 | ON/OFF of the light | Light | Boolean
R.1.258 | /TM023_3_21_1.204/Light_level_1.258 | LN01 | Light level setpoint | Light | %
R.1.258 | /TM023_3_21_1.204/PIR_activity_1.258 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.258 | /TM023_3_21_1.204/Room_temperature_1.258 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.258 | /TM023_3_21_1.204/CO2_level_1.258 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.258 | /TM023_3_21_1.204/Window_position_1.258 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/CO2_setpoint_1.258 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Light_off_switch_high_lux_1.258 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Lux_level_ceiling_1.258 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Lux_level_setpoint_1.258 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Manual_light_on_off_switch_1.258 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Light_automatic_off_delay_1.258 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Ventilation_off_delay_1.258 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.258 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Heating_valve_1.258 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Temperature_offset_from_global_1.258 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Temperature_cooling_setpoint_1.258 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Temperature_heating_setpoint_1.258 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Temperature_global_setpoint_1.258 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.260 | /TM023_3_21_1.204/Damper_position_1.260 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.260 | /TM023_3_21_1.204/Lux_meter_1.260 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.260 | /TM023_3_21_1.204/Light_ON_OFF_1.260 | LY01 | ON/OFF of the light | Light | Boolean
R.1.260 | /TM023_3_21_1.204/Light_level_1.260 | LN01 | Light level setpoint | Light | %
R.1.260 | /TM023_3_21_1.204/PIR_activity_1.260 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.260 | /TM023_3_21_1.204/Room_temperature_1.260 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.260 | /TM023_3_21_1.204/CO2_level_1.260 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.260 | /TM023_3_21_1.204/Window_position_1.260 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/CO2_setpoint_1.260 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Light_off_switch_high_lux_1.260 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Lux_level_ceiling_1.260 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Lux_level_setpoint_1.260 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Manual_light_on_off_switch_1.260 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Light_automatic_off_delay_1.260 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Ventilation_off_delay_1.260 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.260 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Heating_valve_1.260 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Temperature_offset_from_global_1.260 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Temperature_cooling_setpoint_1.260 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Temperature_heating_setpoint_1.260 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Temperature_global_setpoint_1.260 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.263 | /TM023_3_21_1.204/Damper_position_1.263 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.263 | /TM023_3_21_1.204/Lux_meter_1.263 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.263 | /TM023_3_21_1.204/Light_ON_OFF_1.263 | LY01 | ON/OFF of the light | Light | Boolean
R.1.263 | /TM023_3_21_1.204/Light_level_1.263 | LN01 | Light level setpoint | Light | %
R.1.263 | /TM023_3_21_1.204/PIR_activity_1.263 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.263 | /TM023_3_21_1.204/Room_temperature_1.263 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.263 | /TM023_3_21_1.204/CO2_level_1.263 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/CO2_setpoint_1.263 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Light_off_switch_high_lux_1.263 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/PIR_1.263 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Lux_level_setpoint_1.263 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Manual_light_on_off_switch_1.263 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Light_automatic_off_delay_1.263 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Ventilation_off_delay_1.263 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Ventilation_AHU_status_1.263 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Heating_valve_1.263 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Temperature_offset_from_global_1.263 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Temperature_cooling_setpoint_1.263 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Temperature_heating_setpoint_1.263 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Temperature_global_setpoint_1.263 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Damper_VAV | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Light_sensor | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Light_on_off | LY01 | ON/OFF of the light | Light | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Light_level_room | LN01 | Light level setpoint | Light | %
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Motor_valve_heating | TA01 | Opening signal of the radiator valve | Heating | %
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Heating_setpoint | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Cooling_setpoint | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Offset_STR | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp_day_deadband | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp_deadband_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp_deadband_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Runtime_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/CO2_setpoint | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Lux_level_setpoint | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Runtime_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.340 | /TM023_4_22_1.-103C/PIR_activity_1.340 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.340 | /TM023_4_22_1.-103C/Window_position_1.340 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Light_off_switch_high_lux_1.340 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Manual_light_on_off_switch_1.340 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lux_meter_1.340 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Ventilation_AHU_status_1.340 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Damper_VAV | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Light_sensor | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Light_on_off | LY01 | ON/OFF of the light | Light | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Light_level_room | LN01 | Light level setpoint | Light | %
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Motor_valve_heating | TA01 | Opening signal of the radiator valve | Heating | %
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Heating_setpoint | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Cooling_setpoint | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Offset_STR | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp_day_deadband | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp_deadband_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp_deadband_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Runtime_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/CO2_setpoint | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Lux_level_setpoint | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Runtime_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.342 | /TM023_4_22_1.-103C/PIR_activity_1.342 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.342 | /TM023_4_22_1.-103C/Window_position_1.342 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lux_meter_1.342 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Light_off_switch_high_lux_1.342 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Manual_light_on_off_switch_1.342 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Ventilation_AHU_status_1.342 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.344 | /TM023_4_22_1.-103C/Light_ON_OFF_1.344 | LY01 | ON/OFF of the light | Light | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Activity_in_the_room | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/CO2_set-point | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Cooling_set-point | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Heating_radiator_valve | TA01 | Opening signal of the radiator valve | Heating | %
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Heating_set-point | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_delayed_stop | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_level | LN01 | Light level setpoint | Light | %
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_level_in_the_ceiling | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_level_set-point | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_off_switch | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_roompanel | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature_global_deadzone_day | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature_global_deadzone_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature_global_deadzone_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature_globel_set-point | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Temperature_offset_from_STR_panel | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Ventilation_damper_position | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Ventilation_delayed_stop_ | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Ventilation_status | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Window_status | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lux_meter_1.344 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Damper_VAV | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Light_sensor | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Light_on_off | LY01 | ON/OFF of the light | Light | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Light_level_room | LN01 | Light level setpoint | Light | %
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Motor_valve_heating | TA01 | Opening signal of the radiator valve | Heating | %
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Heating_setpoint | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Cooling_setpoint | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Offset_STR | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp_day_deadband | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp_deadband_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp_deadband_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Runtime_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/CO2_setpoint | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Lux_level_setpoint | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Runtime_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.346 | /TM023_4_22_1.-103C/PIR_activity_1.346 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.346 | /TM023_4_22_1.-103C/Window_position_1.346 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lux_meter_1.346 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Light_off_switch_high_lux_1.346 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Manual_light_on_off_switch_1.346 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Ventilation_AHU_status_1.346 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.348 | /TM023_4_22_1.-103C/Damper_inlet_vav | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.348 | /TM023_4_22_1.-103C/Light_sensor | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.348 | /TM023_4_22_1.-103C/Light_on_off | LY01 | ON/OFF of the light | Light | Boolean
R.1.348 | /TM023_4_22_1.-103C/Light_level_room | LN01 | Light level setpoint | Light | %
R.1.348 | /TM023_4_22_1.-103C/Motor_valve_heating | TA01 | Opening signal of the radiator valve | Heating | %
R.1.348 | /TM023_4_22_1.-103C/Room_temp | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.348 | /TM023_4_22_1.-103C/Heating_setpoint | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Cooling_setpoint | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Offset_STR | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Room_temp_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Room_temp_day_deadband | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Room_temp_deadband_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Room_temp_deadband_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Runtime_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.348 | /TM023_4_22_1.-103C/CO2_setpoint | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.348 | /TM023_4_22_1.-103C/Lux_level_setpoint | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.348 | /TM023_4_22_1.-103C/Runtime_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.348 | /TM023_4_22_1.-103C/PIR_activity_1.348 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.348 | /TM023_4_22_1.-103C/Window_position_1.348 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.348 | /TM023_4_22_1.-103C/Lux_meter_1.348 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.348 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.348/Light_off_switch_high_lux_1.348 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.348 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.348/Manual_light_on_off_switch_1.348 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.348 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.348/Ventilation_AHU_status_1.348 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.350 | /TM023_4_22_1.-103C/Damper_position_1.350 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.350 | /TM023_4_22_1.-103C/Lux_meter_1.350 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.350 | /TM023_4_22_1.-103C/Light_ON_OFF_1.350 | LY01 | ON/OFF of the light | Light | Boolean
R.1.350 | /TM023_4_22_1.-103C/Light_level_1.350 | LN01 | Light level setpoint | Light | %
R.1.350 | /TM023_4_22_1.-103C/PIR_activity_1.350 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.350 | /TM023_4_22_1.-103C/Room_temperature_1.350 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.350 | /TM023_4_22_1.-103C/CO2_level_1.350 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.350 | /TM023_4_22_1.-103C/Window_position_1.350 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/CO2_setpoint_1.350 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Light_off_switch_high_lux_1.350 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Lux_level_ceiling_1.350 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Lux_level_setpoint_1.350 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Manual_light_on_off_switch_1.350 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Light_automatic_off_delay_1.350 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Ventilation_off_delay_1.350 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Ventilation_AHU_status_1.350 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Heating_valve_1.350 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Temperature_offset_from_global_1.350 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Temperature_cooling_setpoint_1.350 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Temperature_heating_setpoint_1.350 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Temperature_global_setpoint_1.350 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/Damper_position_1.352 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.352 | /TM023_4_22_1.-103C/Lux_meter_1.352 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.352 | /TM023_4_22_1.-103C/Light_ON_OFF_1.352 | LY01 | ON/OFF of the light | Light | Boolean
R.1.352 | /TM023_4_22_1.-103C/Light_level_1.352 | LN01 | Light level setpoint | Light | %
R.1.352 | /TM023_4_22_1.-103C/PIR_activity_1.352 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.352 | /TM023_4_22_1.-103C/Room_temperature_1.352 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/CO2_level_1.352 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.352 | /TM023_4_22_1.-103C/Window_position_1.352 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/CO2_setpoint_1.352 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Light_off_switch_high_lux_1.352 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Lux_level_ceiling_1.352 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Lux_level_setpoint_1.352 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Manual_light_on_off_switch_1.352 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Light_automatic_off_delay_1.352 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Ventilation_off_delay_1.352 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Ventilation_AHU_status_1.352 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Heating_valve_1.352 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Temperature_offset_from_global_1.352 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Temperature_cooling_setpoint_1.352 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Temperature_heating_setpoint_1.352 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Temperature_global_setpoint_1.352 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/Damper_position_1.354 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.354 | /TM023_4_22_1.-103C/Lux_meter_1.354 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.354 | /TM023_4_22_1.-103C/Light_ON_OFF_1.354 | LY01 | ON/OFF of the light | Light | Boolean
R.1.354 | /TM023_4_22_1.-103C/Light_level_1.354 | LN01 | Light level setpoint | Light | %
R.1.354 | /TM023_4_22_1.-103C/PIR_activity_1.354 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.354 | /TM023_4_22_1.-103C/Room_temperature_1.354 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/CO2_level_1.354 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.354 | /TM023_4_22_1.-103C/Window_position_1.354 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/CO2_setpoint_1.354 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Light_off_switch_high_lux_1.354 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Lux_level_ceiling_1.354 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Lux_level_setpoint_1.354 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Manual_light_on_off_switch_1.354 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Light_automatic_off_delay_1.354 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Ventilation_off_delay_1.354 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Ventilation_AHU_status_1.354 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Heating_valve_1.354 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Temperature_offset_from_global_1.354 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Temperature_cooling_setpoint_1.354 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Temperature_heating_setpoint_1.354 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Temperature_global_setpoint_1.354 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/Damper_position_1.359 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.359 | /TM023_4_22_1.-103C/Lux_meter_1.359 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.359 | /TM023_4_22_1.-103C/Light_ON_OFF_1.359 | LY01 | ON/OFF of the light | Light | Boolean
R.1.359 | /TM023_4_22_1.-103C/Light_level_1.359 | LN01 | Light level setpoint | Light | %
R.1.359 | /TM023_4_22_1.-103C/PIR_activity_1.359 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.359 | /TM023_4_22_1.-103C/Room_temperature_1.359 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/CO2_level_1.359 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/CO2_setpoint_1.359 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Light_off_switch_high_lux_1.359 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Lux_level_ceiling_1.359 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Lux_level_setpoint_1.359 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Manual_light_on_off_switch_1.359 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Light_automatic_off_delay_1.359 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Ventilation_off_delay_1.359 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Heating_valve_1.359 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Temperature_offset_from_global_1.359 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Temperature_cooling_setpoint_1.359 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Temperature_heating_setpoint_1.359 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Temperature_global_setpoint_1.359 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/Damper_position_1.361 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.361 | /TM023_4_22_1.-103C/Lux_meter_1.361 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.361 | /TM023_4_22_1.-103C/Light_ON_OFF_1.361 | LY01 | ON/OFF of the light | Light | Boolean
R.1.361 | /TM023_4_22_1.-103C/Light_level_1.361 | LN01 | Light level setpoint | Light | %
R.1.361 | /TM023_4_22_1.-103C/PIR_activity_1.361 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.361 | /TM023_4_22_1.-103C/Room_temperature_1.361 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/CO2_level_1.361 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.361 | /TM023_4_22_1.-103C/Window_position_1.361 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/CO2_setpoint_1.361 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Light_off_switch_high_lux_1.361 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Lux_level_ceiling_1.361 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Lux_level_setpoint_1.361 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Manual_light_on_off_switch_1.361 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Light_automatic_off_delay_1.361 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Ventilation_off_delay_1.361 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Ventilation_AHU_status_1.361 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Heating_valve_1.361 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Temperature_offset_from_global_1.361 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Temperature_cooling_setpoint_1.361 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Temperature_heating_setpoint_1.361 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Temperature_global_setpoint_1.361 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/Damper_position_1.363 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.363 | /TM023_4_22_1.-103C/Lux_meter_1.363 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.363 | /TM023_4_22_1.-103C/Light_ON_OFF_1.363 | LY01 | ON/OFF of the light | Light | Boolean
R.1.363 | /TM023_4_22_1.-103C/Light_level_1.363 | LN01 | Light level setpoint | Light | %
R.1.363 | /TM023_4_22_1.-103C/PIR_activity_1.363 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.363 | /TM023_4_22_1.-103C/Room_temperature_1.363 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/CO2_level_1.363 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.363 | /TM023_4_22_1.-103C/Window_position_1.363 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/CO2_setpoint_1.363 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Light_off_switch_high_lux_1.363 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Lux_level_ceiling_1.363 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Lux_level_setpoint_1.363 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Manual_light_on_off_switch_1.363 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Light_automatic_off_delay_1.363 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Ventilation_off_delay_1.363 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Ventilation_AHU_status_1.363 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Heating_valve_1.363 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Temperature_offset_from_global_1.363 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Temperature_cooling_setpoint_1.363 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Temperature_heating_setpoint_1.363 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Temperature_global_setpoint_1.363 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/Damper_position_1.365 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.365 | /TM023_4_22_1.-103C/Lux_meter_1.365 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.365 | /TM023_4_22_1.-103C/Light_ON_OFF_1.365 | LY01 | ON/OFF of the light | Light | Boolean
R.1.365 | /TM023_4_22_1.-103C/Light_level_1.365 | LN01 | Light level setpoint | Light | %
R.1.365 | /TM023_4_22_1.-103C/PIR_activity_1.365 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.365 | /TM023_4_22_1.-103C/Room_temperature_1.365 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/CO2_level_1.365 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.365 | /TM023_4_22_1.-103C/Window_position_1.365 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/CO2_setpoint_1.365 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Light_off_switch_high_lux_1.365 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Lux_level_ceiling_1.365 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Lux_level_setpoint_1.365 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Manual_light_on_off_switch_1.365 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Light_automatic_off_delay_1.365 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Ventilation_off_delay_1.365 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Ventilation_AHU_status_1.365 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Heating_valve_1.365 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Temperature_offset_from_global_1.365 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Temperature_cooling_setpoint_1.365 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Temperature_heating_setpoint_1.365 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Temperature_global_setpoint_1.365 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/Damper_position_1.367 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.367 | /TM023_4_22_1.-103C/Lux_meter_1.367 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.367 | /TM023_4_22_1.-103C/Light_ON_OFF_1.367 | LY01 | ON/OFF of the light | Light | Boolean
R.1.367 | /TM023_4_22_1.-103C/Light_level_1.367 | LN01 | Light level setpoint | Light | %
R.1.367 | /TM023_4_22_1.-103C/PIR_activity_1.367 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.367 | /TM023_4_22_1.-103C/Room_temperature_1.367 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/CO2_level_1.367 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.367 | /TM023_4_22_1.-103C/Window_position_1.367 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/CO2_setpoint_1.367 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Light_off_switch_high_lux_1.367 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Lux_level_ceiling_1.367 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Lux_level_setpoint_1.367 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Manual_light_on_off_switch_1.367 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Light_automatic_off_delay_1.367 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Ventilation_off_delay_1.367 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Ventilation_AHU_status_1.367 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Heating_valve_1.367 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Temperature_offset_from_global_1.367 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Temperature_cooling_setpoint_1.367 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Temperature_heating_setpoint_1.367 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Temperature_global_setpoint_1.367 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Lon/Net/Damper_inlet | SMIU01 | ON/OFF signal for the supply/extraction damper in CAV supplied rooms | Ventilation | Boolean
R.1.401 | /TM023_4_22_1.-103C/Lux_meter | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.401 | /TM023_4_22_1.-103C/Light_ON_OFF | LY01 | ON/OFF of the light | Light | Boolean
R.1.401 | /TM023_4_22_1.-103C/Light_level | LN01 | Light level setpoint | Light | %
R.1.401 | /TM023_4_22_1.-103C/Activity_PIR | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.401 | /TM023_4_22_1.-103C/Power_switch_light | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.401 | /TM023_4_22_1.-103C/Room_panel_light | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.401 | /TM023_4_22_1.-103C/Room_temperature | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/CO2_sensor | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.401 | /TM023_4_22_1.-103C/Setting_heating_system | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Setting_cooling | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Offset_str_panel | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Ventilation_system_status | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.401 | /TM023_4_22_1.-103C/Motor_valve_heating_system | TA01 | Opening signal of the radiator valve | Heating | %
R.1.401 | /TM023_4_22_1.-103C/Room_temperature_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Setting_room_temp_dead_band_day | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Setting_room_temp_dead_band_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Setting_room_temp_dead_band_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Run_time_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.401 | /TM023_4_22_1.-103C/Setting_co2_sensor | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.401 | /TM023_4_22_1.-103C/Setting_light_level | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.401 | /TM023_4_22_1.-103C/Run_time_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.401 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.401/PIR_1.401 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
1
2
3
4
5
6
7
8
9
10
11
12
12
13
14
15
16
17
18
19
20
21
22
23
24

## Heating systems
Name | Name in JSON file for the SATO platform | Name in BMS system | Variable description | Unit | Number in picture
VA02 | /TM023_0_20_1128/VA02/Control_valve | MVV01_S | Signal for the control valve on the district heating return string | % | 1
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Effect | power_f (energymeter) | Current effect of the district heating supplied to the heating circuit | W | 2
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Energy_Accumulated | elec_whr_f (energymeter) | Accumulated energy use for the district heating | Wh | 3
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Flow | flow_f (energymeter) | Flow of the distrct heating (does not account for the recirculation flow) | l/s | 4
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Operation_hours_accumulated | count_f (energymeter) | Accumulated hours in operation for the heating system | h | 5
VA02 | /TM023_0_20_1128/VA02/Pump_on-off | PV01_K | ON / OFF signal for the circulation pump | Boolean | 6
VA02 | /TM023_0_20_1128/VA02/Pump_start_at_external_temperature_below | PV01_SV_VINTER_TUD01 (settings) | Activate heating system for winter conditions | °C | 7
VA02 | /TM023_0_20_1128/VA02/Pump_stop_at_external_temperature_above | TUD01_SOMMERSTOP_SV (settings) | Deactivate heating system for summer conditions | °C | 8
VA02 | /TM023_0_20_1128/VA02/Return_temperature | TR01 | Return temperature in the heating circuit | °C | 9
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Return_temperature_DH | temp_p (energymeter) | District heating return temperature | °C | 10
VA02 | /TM023_0_20_1128/VA02/Return_temperature_limit_max_deduction | TR01_FRADRAG_MAX_SV (settings) | Maximum deduction for return limit | °C | 11
VA02 | /TM023_0_20_1128/VA02/Return_temperature_max_limit | TR01_SV (settings) | Max limit of the return temperature in the heating circuit | °C | 12
VA02 | /TM023_0_20_1128/VA02/Supply_temperature | TF01 | Supply temperature in the heating circuit | °C | 13
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Supply_temperature_DH | temp_p (energymeter) | District heating supply temperature | °C | 14
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_X | TF01_KURVE_DAG_X (settings) |  | °C | 15
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_X1 | TF01_KURVE_DAG_X1 (settings) |  | °C | 16
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_X2 | TF01_KURVE_DAG_X2 (settings) |  | °C | 17
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_X3 | TF01_KURVE_DAG_X3 (settings) |  | °C | 18
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_Y | TF01_KURVE_DAG (settings) | Supply temperature for the heating circuit, without offset or additions | °C | 19
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_Y1 | TF01_KURVE_DAG_Y1 (settings) |  | °C | 20
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_Y2 | TF01_KURVE_DAG_Y2 (settings) |  | °C | 21
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_Y3 | TF01_KURVE_DAG_Y3 (settings) |  | °C | 22
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_displacement | TF01_FORSKYD_SV (settings) | Offset for the supply temperature in the heating circuit | °C | 23
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_X | TF01_KURVE_NAT_X (settings) |  | °C | 24
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_X1 | TF01_KURVE_NAT_X1 (settings) |  | °C | 25
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_X2 | TF01_KURVE_NAT_X2 (settings) |  | °C | 26
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_X3 | TF01_KURVE_NAT_X3 (settings) |  | °C | 27
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_Y | TF01_KURVE_NAT | Temperature to lower the supply temperature with during night setback | °C | 28
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_Y1 | TF01_KURVE_NAT_Y1 (settings) |  | °C | 29
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_Y2 | TF01_KURVE_NAT_Y2 (settings) |  | °C | 30
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_Y3 | TF01_KURVE_NAT_Y3 (settings) |  | °C | 31
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_set-point | TF01_KALK_SV | Setpoint for the supply temperature in the heating circuit | °C | 32
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Volume_accumulated | vol_f (energymeter) | Accumulated volume for the district heating | l | 33
1
2
3
4
5
6
7
8
9
10
11
13
14
15 - 22
32
33
23
12
24 - 31