## log_map
Room | Logged_variable_name | Comment | Log_variable_location | Has been moved from original location | Graph_name | Graph_location | Name in BMS system (location if not in the main page of the room/system) | Zone | Level | Logging interval [m] | Number of points in the log | Log period [days] | second sent in BMS
BK01_KVM01 | DCW_whole_building_volume | Domestic cold water accumulated volume supplied to the whole building | /TM023_0_20_1128/Lon/Net/BK01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Volume_Raw
BK01_KVM01 | DCW_whole_building_flow | Domestic cold water current flow supplied to the whole building | /TM023_0_20_1128/Lon/Net/BK01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Flow
BK01_KVM01 | DCW_whole_building_operation_hours | Domestic cold water accumulated number of operation hours for the whole building | /TM023_0_20_1128/Lon/Net/BK01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoHourCount
DØR01_QMV01 | Energi_air_heating_blanket_DØR01 | District heating accumulated energy supplied to the air heating blanket | /TM023_1_20_1103/Lon/Net/DØR01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoE1_HeatV1
DØR01_QMV01 | Volume_accumulated_air_heating_blanket_DØR01 | Accumulated volume for the air heating blanket | /TM023_1_20_1103/Lon/Net/DØR01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | vol_f (energymeter)
DØR01_QMV01 | Effect_air_heating_blanket_DØR01 | Current effect of the district heating supplied to the air heating blanket | /TM023_1_20_1103/Lon/Net/DØR01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | power_f (energymeter)
DØR01_QMV01 | Flow_air_heating_blanket_DØR01 | Flow of the air heating blanket | /TM023_1_20_1103/Lon/Net/DØR01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | flow_f (energymeter)
DØR01_QMV01 | Supply_temperature_air_heating_blanket_DØR01 | Supply temperature in the air heating blanket | /TM023_1_20_1103/Lon/Net/DØR01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | TF01
DØR01_QMV01 | Return_temperature_air_heating_blanket_DØR01 | Return temperature in the air heating blanket | /TM023_1_20_1103/Lon/Net/DØR01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | TR01
DØR01_QMV01 | Operation_hours_accumulated_air_heating_blanket_DØR01 | Accumulated hours in operation for the air heating blanket | /TM023_1_20_1103/Lon/Net/DØR01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | count_f (energymeter)
El Ladestation 1 Energy | El Ladestation 1 Energy | Ladestation 1 | /TM023_1_20_1101/Lon/Net/El Ladestation 1/EnergyMeter63A/EnergyMeas [1]
El Ladestation 1 Power | El Ladestation 1 Power | Ladestation 1 | /TM023_1_20_1101/Lon/Net/El Ladestation 1/EnergyMeter63A/RMSMeas [20001]
El Ladestation 2 Energy | El Ladestation 2 Energy | Ladestation 2 | /TM023_1_20_1101/Lon/Net/El Ladestation 2/EnergyMeter63A/EnergyMeas [1]
El Ladestation 2 Power | El Ladestation 2 Power | Ladestation 2 | /TM023_1_20_1101/Lon/Net/El Ladestation 2/EnergyMeter63A/RMSMeas [20001]
ET01_VVB01_KVM01 Timer | ET01_VVB01_KVM01 Timer | Varmt brugsvand | /TM023_1_20_1103/Lon/Net/VVB01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET01_VVB02_KVM02 Timer | ET01_VVB02_KVM02 Timer | Varmt brugsvand | /TM023_1_20_1101/Lon/Net/VVB02_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET01-V-C22.1 Energy | ET01-V-C22.1 Energy | Sektion Processenergi | /TM023_1_20_1101/Lon/Net/ET01-V-C22.1/EnergyMeter5A/EnergyMeas [1]
ET01-V-C22.1 Power | ET01-V-C22.1 Power | Sektion Processenergi | /TM023_1_20_1101/Lon/Net/ET01-V-C22.1/EnergyMeter5A/RMSMeas [20001]
ET01-V-C222.1 Energy | ET01-V-C222.1 Energy | Sektion Bygningsenergi | /TM023_1_20_1101/Lon/Net/ET01-V-C222.1/EnergyMeter5A/EnergyMeas [1]
ET01-V-C222.1 Power | ET01-V-C222.1 Power | Sektion Bygningsenergi | /TM023_1_20_1101/Lon/Net/ET01-V-C222.1/EnergyMeter5A/RMSMeas [20001]
ET01-V-C301.1 Energy | ET01-V-C301.1 Energy | Sektion Belysnings energi | /TM023_1_20_1101/Lon/Net/ET01-V-C301.1/EnergyMeter5A/EnergyMeas [1]
ET01-V-C301.1 Power | ET01-V-C301.1 Power | Sektion Belysnings energi | /TM023_1_20_1101/Lon/Net/ET01-V-C301.1/EnergyMeter5A/RMSMeas [20001]
ET01-Ø-C22.1 Energy | ET01-Ø-C22.1 Energy | Sektion Processenergi | /TM023_1_20_1103/Lon/Net/ET01-Ø-C22.1/EnergyMeter5A/EnergyMeas [1]
ET01-Ø-C22.1 Power | ET01-Ø-C22.1 Power | Sektion Processenergi | /TM023_1_20_1103/Lon/Net/ET01-Ø-C22.1/EnergyMeter5A/RMSMeas [20001]
ET01-Ø-C23.1 Energy | ET01-Ø-C23.1 Energy | Ventilation LAB01 | /TM023_1_20_1103/Lon/Net/ET01-Ø-C23.1/EnergyMeter63A/EnergyMeas [1]
ET01-Ø-C232.1 Energy | ET01-Ø-C232.1 Energy | Sektion Bygningsenergi | /TM023_1_20_1103/Lon/Net/ET01-Ø-C232.1/EnergyMeter5A/EnergyMeas [1]
ET01-Ø-C232.1 Power | ET01-Ø-C232.1 Power | Sektion Bygningsenergi | /TM023_1_20_1103/Lon/Net/ET01-Ø-C232.1/EnergyMeter5A/RMSMeas [20001]
ET01-Ø-C24.1 Energy | ET01-Ø-C24.1 Energy | Ventilation LAB02 | /TM023_1_20_1103/Lon/Net/ET01-Ø-C24.1/EnergyMeter63A/EnergyMeas [1]
ET01-Ø-C301.1 Energy | ET01-Ø-C301.1 Energy | Sektion Belysnings energi | /TM023_1_20_1103/Lon/Net/ET01-Ø-C301.1/EnergyMeter5A/EnergyMeas [1]
ET01-Ø-C301.1 Power | ET01-Ø-C301.1 Power | Sektion Belysnings energi | /TM023_1_20_1103/Lon/Net/ET01-Ø-C301.1/EnergyMeter5A/RMSMeas [20001]
ET02_VVB01_KVM01 Timer | ET02_VVB01_KVM01 Timer | Varmt brugsvand | /TM023_2_20_1.103B/Lon/Net/VVB01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET02_VVB02_KVM02 Timer | ET02_VVB02_KVM02 Timer | Varmt brugsvand | /TM023_2_20_1.103B/Lon/Net/VVB02_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET03_VVB01_KVM01 Timer | ET03_VVB01_KVM01 Timer | Varmt brugsvand | /TM023_3_21_1.204/Lon/Net/VVB01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET03_VVB02 | ET03_VVB02_KVM01 | Volume of added cold water | /ES01/Thomas Manns Vej/TM023/MålerLog
ET03_VVB02 | nvoV1_Flow Log | Flow of added cold water | /TM023_3_21_1.204/Lon/Net/VVB02_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET03_VVB02_KVM02 Timer | ET03_VVB02_KVM02 Timer | Varmt brugsvand | /TM023_3_21_1.204/Lon/Net/VVB02_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET04_VVB01_KVM01 Timer | ET04_VVB01_KVM01 Timer | Varmt brugsvand | /TM023_4_22_1.-103C/Lon/Net/VVB01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET04_VVB02_KVM02 Timer | ET04_VVB02_KVM02 Timer | Varmt brugsvand | /TM023_4_22_1.-103C/Lon/Net/VVB02_KMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET04_VVB02_QVM01 Aktuel Effekt | ET04_VVB02_QVM01 Aktuel Effekt | Fjernvarme brugsvand | /TM023_4_22_1.-103C/Lon/Net/VVB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET04_VVB02_QVM01 Energi | ET04_VVB02_QVM01 Energi | Fjernvarme brugsvand | /TM023_4_22_1.-103C/Lon/Net/VVB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET04_VVB02_QVM01 Flow | ET04_VVB02_QVM01 Flow | Fjernvarme brugsvand | /TM023_4_22_1.-103C/Lon/Net/VVB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET04_VVB02_QVM01 Frem temp | ET04_VVB02_QVM01 Frem temp | Fjernvarme brugsvand | /TM023_4_22_1.-103C/Lon/Net/VVB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET04_VVB02_QVM01 Retur temp | ET04_VVB02_QVM01 Retur temp | Fjernvarme brugsvand | /TM023_4_22_1.-103C/Lon/Net/VVB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET04_VVB02_QVM01 Timer | ET04_VVB02_QVM01 Timer | Fjernvarme brugsvand | /TM023_4_22_1.-103C/Lon/Net/VVB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET04_VVB02_QVM01 Volumen | ET04_VVB02_QVM01 Volumen | Fjernvarme brugsvand | /TM023_4_22_1.-103C/Lon/Net/VVB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
ET05-V-C201.1 Energy | ET05-V-C201.1 Energy | Sektions bygningsenergi | /TM023_4_22_1.-103C/Lon/Net/ET05-V-C201.1/EnergyMeter5A/EnergyMeas [1]
ET05-V-C201.1 Power | ET05-V-C201.1 Power | Sektions bygningsenergi | /TM023_4_22_1.-103C/Lon/Net/ET05-V-C201.1/EnergyMeter5A/RMSMeas [20001]
ET05-V-C21.1 Energy | ET05-V-C21.1 Energy | Sektions processenergi | /TM023_4_22_1.-103C/Lon/Net/ET05-V-C21.1/EnergyMeter5A/EnergyMeas [1]
ET05-V-C21.1 Power | ET05-V-C21.1 Power | Sektions processenergi | /TM023_4_22_1.-103C/Lon/Net/ET05-V-C21.1/EnergyMeter5A/RMSMeas [20001]
ET05-V-C301.1 Energy | ET05-V-C301.1 Energy | Sektions belysningsenergi | /TM023_4_22_1.-103C/Lon/Net/ET05-V-C301.1/EnergyMeter5A/EnergyMeas [1]
ET05-V-C301.1 Power | ET05-V-C301.1 Power | Sektions belysningsenergi | /TM023_4_22_1.-103C/Lon/Net/ET05-V-C301.1/EnergyMeter5A/RMSMeas [20001]
FO01_QMV01 | DH_whole_building_energy | District heating accumulated energy supplied for the whole building | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoE1_HeatV1_Raw
FO01_QMV01 | DH_whole_building_volume | District heating accumulated volume supplied for the whole building | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Volume_Raw
FO01_QMV01 | DH_whole_building_power | District heating power currently supplied to the whole building | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoPowerV1
FO01_QMV01 | DH_whole_building_flow | District heating flow currently supplied to the whole building | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Flow
FO01_QMV01 | DH_whole_building_supply_temperature | District heating supply temperature currently supplied to the whole building | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature1
FO01_QMV01 | DH_whole_building_return_temperature | District heating return temperature currently supplied from the whole building | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature2
FO01_QMV01 | DH_whole_building_operation_hours | District heating accumulated number of operation hours for the whole building | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoHourCount
G.1.102 West | Lux_meter_G.1.102 | Light sensor | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | LUX01 |  |  | 1 | 11000 | 7.6389
G.1.102 West | Light_ON_OFF_G.1.102 | Light ON/OFF | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | LY01 |  |  | 1 | 11000 | 7.6389
G.1.102 West | Light_level_G.1.132 | Light level in the room | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | LN01 |  |  | 1 | 11000 | 7.6389
G.1.102 West | PIR_activity_G.1.102 | activity in the room | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | ZoneAktiv |  |  | 1 | 11000 | 7.6389
G.1.102 West | Room_temperature_G.1.102 | Room temperature | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | TRU01 |  |  | 1 | 11000 | 7.6389
G1.003 | PIR_Activity_1.003 | If the room is considered active | /TM023_1_20_1101/Lon/Net/Rum 1.G1.003 |  |  |  | ZoneAktiv | [5 empty] | 9
G1.004 | PIR_Activity_1.004 | If the room is considered active | /TM023_1_20_1101/Lon/Net/Rum 1.024/XENTA |  |  |  | ZoneAktiv | [5 empty] | 11
G1.024 | PIR_Activity_1.024 | If the room is considered active | /TM023_1_20_1101/Lon/Net/Rum 1.024 |  |  |  | ZoneAktiv | [5 empty] | 10
G1.101 | PIR_Activity_1.101 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum G1.101 |  |  |  | ZoneAktiv | [5 empty] | 22
G1.102 Vest | PIR_Activity_1.102_Vest | If the room is considered active | /TM023_2_20_1.103B/G 1.102 Vest (OSB: NOTE1) |  |  |  | ZoneAktiv | [5 empty] | 23
G1.102 Øst | PIR_Activity_1.102_est | If the room is considered active | /TM023_2_20_1.103B/G 1.102 Øst |  |  |  | ZoneAktiv | [5 empty] | 24
GV01_QMV01 | Energi_floorheating_GV01 | District heating accumulated energy supplied to floorheating for foyer | /TM023_0_20_1.011/Lon/Net/GV01-QMV01/KamstrupHeatKMP/Node Object [0] |  |  |  | nvoE1_HeatV1
GV01_QMV01 | DH_volume_GV01 | District heating accumulated volume supplied to floorheating for foyer | /TM023_0_20_1.011/Lon/Net/GV01-QMV01/KamstrupHeatKMP/Node Object [0] |  |  |  | nvoV1_Volume_Raw
GV01_QMV01 | DH_effekt_GV01 | District heating power currently supplied to floorheating for foyer | /TM023_0_20_1.011/Lon/Net/GV01-QMV01/KamstrupHeatKMP/Node Object [0] |  |  |  | nvoPowerV1
GV01_QMV01 | DH_flow_GV01 | District heating flow currently supplied to floorheating for foyer | /TM023_0_20_1.011/Lon/Net/GV01-QMV01/KamstrupHeatKMP/Node Object [0] |  |  |  | nvoV1_Flow
GV01_QMV01 | DH_supply_temperature_GV01 | District heating supply temperature currently supplied to floorheating for foyer | /TM023_0_20_1.011/Lon/Net/GV01-QMV01/KamstrupHeatKMP/Node Object [0] |  |  |  | nvoTemperature1
GV01_QMV01 | DH_return_temperature_GV01 | District heating return temperature currently supplied to floorheating for foyer | /TM023_0_20_1.011/Lon/Net/GV01-QMV01/KamstrupHeatKMP/Node Object [0] |  |  |  | nvoTemperature2
GV01_QMV01 | DH_operation_hours_GV01 | District heating accumulated number of operation hours for floorheating for foyer | /TM023_0_20_1.011/Lon/Net/GV01-QMV01/KamstrupHeatKMP/Node Object [0] |  |  |  | nvoHourCount
GV02_QMV01 | Energi_floorheating_GV02 | District heating accumulated energy supplied to floorheating for basement | /TM023_0_20_1110/Lon/Net/GV02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoE1_HeatV1
GV02_QMV01 | DH_volume_GV02 | District heating accumulated volume supplied to floorheating for basement | /TM023_0_20_1110/Lon/Net/GV02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Volume_Raw
GV02_QMV01 | DH_effekt_GV02 | District heating power currently supplied to floorheating for basement | /TM023_0_20_1110/Lon/Net/GV02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoPowerV1
GV02_QMV01 | DH_flow_GV02 | District heating flow currently supplied to floorheating for basement | /TM023_0_20_1110/Lon/Net/GV02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Flow
GV02_QMV01 | DH_supply_temperature_GV02 | District heating supply temperature currently supplied to floorheating for basement | /TM023_0_20_1110/Lon/Net/GV02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature1
GV02_QMV01 | DH_return_temperature_GV02 | District heating return temperature currently supplied to floorheating for basement | /TM023_0_20_1110/Lon/Net/GV02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature2
GV02_QMV01 | DH_operation_hours_GV02 | District heating accumulated number of operation hours for floorheating for basement | /TM023_0_20_1110/Lon/Net/GV02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoHourCount
HT00-1_EM01 | EL_whole_building_power | Electrical power supplied to the whole building | /TM023_0_20_1121/Modbus Com B/HT.00-1-EM01/PM710/Modbus Signals |  |  |  | Real Power, Total
HT00-1_EM01 | EL_whole_building_energy | Accumulated electrical energy supplied to the whole building | /TM023_0_20_1121/Modbus Com B/HT.00-1-EM01/PM710/Modbus Signals |  |  |  | Signed Real Energy, Consumption
HT00-1-C102.1 Energy | HT00-1-C102.1 Energy | Procesenergi Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C102.1/EnergyMeter/EnergyMeas [1]
HT00-1-C102.1 Power | HT00-1-C102.1 Power | Procesenergi Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C102.1/EnergyMeter/RMSMeas [20001]
HT00-1-C113.1 Energy | HT00-1-C113.1 Energy | Kølemaskine Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C113.1/EnergyMeter/EnergyMeas [1]
HT00-1-C113.1 Power | HT00-1-C113.1 Power | Kølemaskine Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C113.1/EnergyMeter/RMSMeas [20001]
HT00-1-C124.1 Energy | HT00-1-C124.1 Energy | Kølemaskine Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C124.1/EnergyMeter/EnergyMeas [1]
HT00-1-C124.1 Power | HT00-1-C124.1 Power | Kølemaskine Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C124.1/EnergyMeter/RMSMeas [20001]
HT00-1-C126.1 Energy | HT00-1-C126.1 Energy | Køl klima Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C126.1/EnergyMeter/EnergyMeas [1]
HT00-1-C126.1 Power | HT00-1-C126.1 Power | Køl klima Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C126.1/EnergyMeter/RMSMeas [20001]
HT00-1-C127.1 Energy | HT00-1-C127.1 Energy | Køl klima Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C127.1/EnergyMeter/EnergyMeas [1]
HT00-1-C127.1 Power | HT00-1-C127.1 Power | Køl klima Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C127.1/EnergyMeter/RMSMeas [20001]
HT00-1-C132.1 Energy | HT00-1-C132.1 Energy | Køl klima Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C132.1/EnergyMeter/EnergyMeas [1]
HT00-1-C132.1 Power | HT00-1-C132.1 Power | Køl klima Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C132.1/EnergyMeter/RMSMeas [20001]
HT00-1-C133.1 Energy | HT00-1-C133.1 Energy | Køl klima Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C133.1/EnergyMeter/EnergyMeas [1]
HT00-1-C133.1 Power | HT00-1-C133.1 Power | Køl klima Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C133.1/EnergyMeter/RMSMeas [20001]
HT00-1-C134.1 Energy | HT00-1-C134.1 Energy | Køl klima Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C134.1/EnergyMeter/EnergyMeas [1]
HT00-1-C134.1 Power | HT00-1-C134.1 Power | Køl klima Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C134.1/EnergyMeter/RMSMeas [20001]
HT00-1-C202.1 Energy | HT00-1-C202.1 Energy | Bygningsenergi Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C202.1/EnergyMeter/EnergyMeas [1]
HT00-1-C202.1 Power | HT00-1-C202.1 Power | Bygningsenergi Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C202.1/EnergyMeter/RMSMeas [20001]
HT00-1-C203.1 Energy | HT00-1-C203.1 Energy | Person elevator Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C203.1/EnergyMeter/EnergyMeas [1]
HT00-1-C203.1 Power | HT00-1-C203.1 Power | Person elevator Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C203.1/EnergyMeter/RMSMeas [20001]
HT00-1-C33.1 Energy | HT00-1-C33.1 Energy | P_Vand Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C33.1/EnergyMeter/EnergyMeas [1]
HT00-1-C33.1 Power | HT00-1-C33.1 Power | P_Vand Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C33.1/EnergyMeter/RMSMeas [20001]
HT00-1-C34.1 Energy | HT00-1-C34.1 Energy | P_klima Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C34.1/EnergyMeter/EnergyMeas [1]
HT00-1-C34.1 Power | HT00-1-C34.1 Power | P_klima Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C34.1/EnergyMeter/RMSMeas [20001]
HT00-1-C35.1 Energy | HT00-1-C35.1 Energy | P_fund Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C35.1/EnergyMeter/EnergyMeas [1]
HT00-1-C35.1 Power | HT00-1-C35.1 Power | P_fund Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C35.1/EnergyMeter/RMSMeas [20001]
HT00-1-C352.1 Energy | HT00-1-C352.1 Energy | Belysningsenergi Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C352.1/EnergyMeter/EnergyMeas [1]
HT00-1-C352.1 Power | HT00-1-C352.1 Power | Belysningsenergi Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C352.1/EnergyMeter/RMSMeas [20001]
HT00-1-C36.1 Energy | HT00-1-C36.1 Energy | P_Værk Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C36.1/EnergyMeter/EnergyMeas [1]
HT00-1-C36.1 Power | HT00-1-C36.1 Power | P_Værk Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C36.1/EnergyMeter/RMSMeas [20001]
HT00-1-C37.1 Energy | HT00-1-C37.1 Energy | Ventilations_tavle Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C37.1/EnergyMeter/EnergyMeas [1]
HT00-1-C37.1 Power | HT00-1-C37.1 Power | Ventilations_tavle Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C37.1/EnergyMeter/RMSMeas [20001]
HT00-1-C41.1 Energy | HT00-1-C41.1 Energy | Solcelle anlæg Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C41.1/EnergyMeter/EnergyMeas [1]
HT00-1-C41.1 Power | HT00-1-C41.1 Power | Solcelle anlæg Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C41.1/EnergyMeter/RMSMeas [20001]
HT00-1-C45.1 Energy | HT00-1-C45.1 Energy | Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C45.1/EnergyMeter/EnergyMeas [1]
HT00-1-C45.1 Power | HT00-1-C45.1 Power | Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C45.1/EnergyMeter/RMSMeas [20001]
HT00-1-C46.1 Energy | HT00-1-C46.1 Energy | Vare elevator Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C46.1/EnergyMeter/EnergyMeas [1]
HT00-1-C46.1 Power | HT00-1-C46.1 Power | Vare elevator Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C46.1/EnergyMeter/RMSMeas [20001]
HT00-1-C51.1 Energy | HT00-1-C51.1 Energy | Vandbehandling Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C51.1/EnergyMeter/EnergyMeas [1]
HT00-1-C51.1 Power | HT00-1-C51.1 Power | Vandbehandling Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C51.1/EnergyMeter/RMSMeas [20001]
HT00-1-C52.1 Energy | HT00-1-C52.1 Energy | Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C52.1/EnergyMeter/EnergyMeas [1]
HT00-1-C52.1 Power | HT00-1-C52.1 Power | Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C52.1/EnergyMeter/RMSMeas [20001]
HT00-1-C53.1 Energy | HT00-1-C53.1 Energy | Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C53.1/EnergyMeter/EnergyMeas [1]
HT00-1-C53.1 Power | HT00-1-C53.1 Power | Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C53.1/EnergyMeter/RMSMeas [20001]
HT00-1-C54.1 Energy | HT00-1-C54.1 Energy | Accumulated energy use | /TM023_0_20_1121/Lon/Net/HT00-1-C54.1/EnergyMeter/EnergyMeas [1]
HT00-1-C54.1 Power | HT00-1-C54.1 Power | Instantainious power use | /TM023_0_20_1121/Lon/Net/HT00-1-C54.1/EnergyMeter/RMSMeas [20001]
HT00-1-F139.1 Energy | HT00-1-F139.1 Energy | Kompressor 1 | /TM023_0_20_1121/Lon/Net/HT00-1-F139.1/EnergyMeter/EnergyMeas [1]
HT00-1-F139.1 Power | HT00-1-F139.1 Power | Kompressor 1 | /TM023_0_20_1121/Lon/Net/HT00-1-F139.1/EnergyMeter/RMSMeas [20001]
HT00-1-F140.1 Energy | HT00-1-F140.1 Energy | Kompressor 2 | /TM023_0_20_1121/Lon/Net/HT00-1-F140.1/EnergyMeter/EnergyMeas [1]
HT00-1-F140.1 Power | HT00-1-F140.1 Power | Kompressor 2 | /TM023_0_20_1121/Lon/Net/HT00-1-F140.1/EnergyMeter/RMSMeas [20001]
KEMI_QMV01 Aktuel Effekt | KEMI_QMV01 Aktuel Effekt | Fjernvarme ventilation KEMI | /TM023_1_21_1031B/Lon/Net/KEMI_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
KEMI_QMV01 Flow | KEMI_QMV01 Flow | Fjernvarme ventilation KEMI | /TM023_1_21_1031B/Lon/Net/KEMI_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
KEMI_QMV01 Frem temp | KEMI_QMV01 Frem temp | Fjernvarme ventilation KEMI | /TM023_1_21_1031B/Lon/Net/KEMI_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
KEMI_QMV01 Retur temp | KEMI_QMV01 Retur temp | Fjernvarme ventilation KEMI | /TM023_1_21_1031B/Lon/Net/KEMI_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
KEMI_QMV01 Timer | KEMI_QMV01 Timer | Fjernvarme ventilation KEMI | /TM023_1_21_1031B/Lon/Net/KEMI_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
KEMI_QMV01 Volumen | KEMI_QMV01 Volumen | Fjernvarme ventilation KEMI | /TM023_1_21_1031B/Lon/Net/KEMI_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
KOMF01 | HC_effect | Current output effect of the heating coil | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | power_f (energymeter) |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_energy_accumulated | Accumulated energy use for the heating coil | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | elec_whr_f (energymeter) |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_flow | Flow over the heating coil (does not account for the recirculated flow) | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | flow_f (energymeter) |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_operation_hours_accumulated | Accumulated hours in operation for the heating coil | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | count_f (energymeter) |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_return_temperature_DH | Temperature of the heating coil water after exiting the HC loop | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | temp_p (energymeter) |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_supply_temperature_DH | Temperature of the heating coil water before entering the HC loop | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | temp_p (energymeter) |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_volume_accumulated | Accumulated flow through the heating coil | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | vol_f (energymeter) |  |  | 1 | 11000 | 7.6389
KOMF01 | Energi_frequency_KOMF01 | Frequency for the electricity meter for the ventilation system | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoFrequency
KOMF01 | Energi_average_voltage_KOMF01 | Voltage for the electricity meter for the ventilation system | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoVoltsLLAvg
KOMF01 | Energi_Current_phase_L1_KOMF01 | Energi of eletrick current of phase 1 | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoCurrentPh1
KOMF01 | Energi_Current_phase_L2_KOMF01 | Energi of eletrick current of phase 2 | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoCurrentPh2
KOMF01 | Energi_Current_phase_L3_KOMF01 | Energi of eletrick current of phase 3 | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoCurrentPh3
KOMF01 | Energi_Total_power_KOMF01 | Total power for the electricity meter for the ventilation system | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoActPowerSum
KOMF01 | nvoPartialkWh Log |  | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/EnergyMeas [1] |  |  |  | nvoTotkWhlmp
KOMF01 | Energi_Total_reactivie_energy_KOMF01 | Total reactive energy for the electricity meter for the ventilation system | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/EnergyMeas [1] |  |  |  | nvoTotkVARhImp
KOMF01 | Air_flow_KOMF01 | Air flow at the exhaust fan | /TM023_0_23_1.125/KOMF01 |  |  |  | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h |  |  | 1 | 11000 | 7.6389
KOMF01 | Pressure_diff_fan | Pressure difference over the exhaust fan | /TM023_0_23_1.125/KOMF01 |  |  |  | SXW_VEN_Rotorveksler_000K/PDU01 |  |  | 1 | 11000 | 7.6389
KOMF01 | Exhaust_fan_start | Exhaust fan on/off signal | /TM023_0_23_1.125/KOMF01 |  |  |  | VU01_K |  |  | 1 | 11000 | 7.6389
KOMF01 | Alarm_filter_exhaust | Alarm at the extraction air filter | /TM023_0_23_1.125/KOMF01 |  |  |  | PFU01_F |  |  | 1 | 11000 | 7.6389
KOMF01 | Alarm_intake_filter | Alarm at the intake air filter | /TM023_0_23_1.125/KOMF01 |  |  |  | PFU01_F |  |  | 1 | 11000 | 7.6389
KOMF01 | ATV_control_supply | Energy use for the supply fan | /TM023_0_23_1.125/KOMF01 |  |  |  | ATV control/FE29 |  |  | 1 | 11000 | 7.6389
KOMF01 | Air_flow_supply | Air flow at the supply fan | /TM023_0_23_1.125/KOMF01 |  |  |  | VI01_FLOW_m3_h |  |  | 1 | 11000 | 7.6389
KOMF01 | Air pressure_diff_supply | Pressure difference over the supply fan | /TM023_0_23_1.125/KOMF01 |  |  |  | PDI01 |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_fan_start | Supply fan on/off signal | /TM023_0_23_1.125/KOMF01 |  |  |  | VI01_K |  |  | 1 | 11000 | 7.6389
KOMF01 | Cooling_recovery_active_if | Temperature difference (outdoor temp above extraction temp) where the cooling recovery activates at | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | KØLIG_DIFF_T_AKT_SV (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Cooling_recovery_inactive_if | Temperature difference (extraction temp above outdoor temp) where the cooling recovery deactivates at | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | KØLIG_DIFF_T_DEAKT_SV (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Exhaust_fan_signal | Rotation speed signal for the exhaust fan | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | VU01_S |  |  | 1 | 11000 | 7.6389
KOMF01 | Exhaust_temperature | Temperature at the exhaust | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TU02 |  |  | 1 | 11000 | 7.6389
KOMF01 | Extraction_damper_on-off | Position of the extraction damper (on/off) | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | SMU01_K |  |  | 1 | 11000 | 7.6389
KOMF01 | Extraction_pressure | Pressure at the extraction point | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | PTU01 |  |  | 1 | 11000 | 7.6389
KOMF01 | Extraction_pressure_set-point | Set-point for the extraction pressure | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | PTU01_SV (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Extraction_temperature | Temperature of the extraction air | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TU01 |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_control_valve | Signal for the control valve on the heating coil | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | MVV01_S |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_pump_on-off | Control signal for the heating coil pump (on/off) | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | PV01_K |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_return_temperature | Temperature of the heating coil water after the HC | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TR01 |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_return_temperature_min_limit | Lowest acceptable heating coil return temperature (anti-freeze) | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TR01_SV (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | HC_supply_temperature | Temperature of the heating coil water before the HC | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TF01 |  |  | 1 | 11000 | 7.6389
KOMF01 | HE_efficiency | Efficiency of the heat exchanger | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | VIRKNINGSGRAD |  |  | 1 | 11000 | 7.6389
KOMF01 | HE_signal | Rotation signal of the heat exchanger | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | RV01_S |  |  | 1 | 11000 | 7.6389
KOMF01 | Intake_damper_on-off | Control signal for the intake damper (on/off) | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | SMI01_K |  |  | 1 | 11000 | 7.6389
KOMF01 | Intake_temperature | Temperature at the intake | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI03 |  |  | 1 | 11000 | 7.6389
KOMF01 | Night_cooling_active_if_diff_external_temperature_and_room_temperature_above | Setpoint for night cooling when outdoor temp < room temp | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | NATKØL_SV_D_TUD_TRU (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Night_cooling_active_if_external_temperature_above | Setpoint for night cooling based on room temp and outdoor temp | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | NATKØL_SV_LAV_TUD01 (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Night_cooling_active_if_room_temperature_above | Setpoint for night cooling based on room temp | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | NATKØL_SV_TRU01 (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Night_cooling_max_operation_hours_per_day | max workning time for the night cooling mode | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | NATKØL_SV_TIM_START (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Night_heating_active_if_room_temperature_below | part of the night cooling control settings | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | NATVARME_SV_TRU01 (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Night_heating_max_operation_hours_per_day | max workning time for the night heating mode | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | NATVAR_SV_TIM_START (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_fan_signal | Rotation speed signal for the supply fan | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | VI01_S |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_pressure | Pressure at the supply point | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | PTI01 |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_pressure_set-point | Set-point for the supply pressure | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | PTI01_SV (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature | Temperature of the supply air | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01 |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature_curve_X | Current outdoor temperature | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_KURVE_X (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature_curve_X1 | Outdoor temperature at control point 1 | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_KURVE_X1 (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature_curve_X2 | Outdoor temperature at control point 2 | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_KURVE_X2 (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature_curve_X3 | Outdoor temperature at control point 3 | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_KURVE_X3 (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature_curve_Y | Current supply temperature set-point without any compensation | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_KURVE (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature_curve_Y1 | Uncompensated supply temperature set-point at control point 1 | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_KURVE_Y1 (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature_curve_Y2 | Uncompensated supply temperature set-point at control point 2 | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_KURVE_Y2 (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature_curve_Y3 | Uncompensated supply temperature set-point at control point 3 | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_KURVE_Y3 (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | Supply_temperature_set-point | Supply temperature set-point (with any additional compensation) | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_KALK_SV |  |  | 1 | 11000 | 7.6389
KOMF01 | Temperature_after_HE_before_HC | Temperature on the supply side after the heat exchanger but before the heating coil | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI02 |  |  | 1 | 11000 | 7.6389
KOMF01 | Winter_mode_active_if_external_temperature_below | Activation temperature of winter mode | /TM023_0_23_1.125/KOMF01 |  | KOMF01 | /TM023_0_23_1.125/KOMF01 | TI01_REG_SV_LAV_UT (settings) |  |  | 1 | 11000 | 7.6389
KOMF01 | ventilation_system_status |  | /TM023_0_23_1.125/KOMF01 |  |  |  | VEN_STATUS
KOMF01 | Setting_Extended_run_time_ventilation_system |  | /TM023_0_23_1.125/KOMF01 |  |  |  | DT01_FORL_DR_TID_SV
KOMF01 | Setting_status_extended_run_time |  | /TM023_0_23_1.125/KOMF01 |  |  |  | DT01_FORL_DRIFT
KOMF01 | Setting_supply_temperature |  | /TM023_0_23_1.125/KOMF01 |  |  |  | TI01_SV
KOMF01 | Setting_desired_room_temperature |  | /TM023_0_23_1.125/KOMF01 |  |  |  | TRU01_SV
KOMF01 | Setting_max_inlet_temp |  | /TM023_0_23_1.125/KOMF01 |  |  |  | TI01_KALK_TRU_MAX_SV
KOMF01 | Setting_min_inlet_temp |  | /TM023_0_23_1.125/KOMF01 |  |  |  | TI01_KALK_TRU_MIN_SV
KOMF01 | Setting_desired_outlet_temp |  | /TM023_0_23_1.125/KOMF01 |  |  |  | TU01_SV
KOMF01 | Setting_max_outlet_temp |  | /TM023_0_23_1.125/KOMF01 |  |  |  | TI01_KALK_TU_MAX_SV
KOMF01 | Setting_min_outlet_temp |  | /TM023_0_23_1.125/KOMF01 |  |  |  | TI01_KALK_TU_MIN_SV
KOMF01 | Temperature_room_1.136 |  | /TM023_0_23_1.125/KOMF01 |  |  |  | 1136_TRU01
KOMF01 | Temperature_room_1.255 |  | /TM023_0_23_1.125/KOMF01 |  |  |  | 1255_TRU01
KOMF01 | Temperature_room_1.365 |  | /TM023_0_23_1.125/KOMF01 |  |  |  | 1365_TRU01
KOMF01 | SEL_value |  | /TM023_0_23_1.125/KOMF01 |  |  |  | SEL_VÆRDI_J_m3
KOMF01 | Heat_coil_alarm |  | /TM023_0_23_1.125/IO Bus/M3_UI-16 |  |  |  | TFI01
KOMF01 | ATV_control | Energy use for the exhaust fan | /TM023_0_23_1.125 |  |  |  | ATV control/FE29 |  |  | 1 | 11000 | 7.6389
KOMF02 | ATV_power_exhaust |  | /TM023_0_20_1.011/ModbusA VEXX/ATV212 KOMF02 VU01 |  |  |  | ATV control/FE29
KOMF02 | ATV_power_supply |  | /TM023_0_20_1.011/ModbusA VEXX/ATV212 KOMF02 VI01 |  |  |  | ATV control/FE29
KOMF02 | Energi_frequency_KOMF02 | Frequency for the electricity meter for the ventilation system | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoFrequency
KOMF02 | Energi_average_voltage_KOMF02 | Voltage for the electricity meter for the ventilation system | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoVoltsLLAvg
KOMF02 | Energi_Current_phase_L1_KOMF02 | Energi of eletrick current of phase 1 | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoCurrentPh1
KOMF02 | Energi_Current_phase_L2_KOMF02 | Energi of eletrick current of phase 2 | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoCurrentPh2
KOMF02 | Energi_Current_phase_L3_KOMF02 | Energi of eletrick current of phase 3 | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoCurrentPh3
KOMF02 | Energi_Total_power_KOMF02 | Total power for the electricity meter for the ventilation system | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoActPowerSum
KOMF02 | nvoPartialkWh Log |  | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/EnergyMeas [1] |  |  |  | nvoTotkWhImp
KOMF02 | Energi_Total_reactivie_energy_KOMF02 | Total reactive energy for the electricity meter for the ventilation system | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/EnergyMeas [1] |  |  |  | nvoTotkVARhImp
KOMF02 | ventilation_system_status | Operation of the ventilation system | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | elec_kwh_l (kWh) |  |  | 1 | 11000 | 7.6389
KOMF02 | Fan_exhaust_status | Operation of the exhaust fan | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | VU01_K |  |  | 1 | 11000 | 7.6389
KOMF02 | Fan_exhaust_speed | Speed of the exhaust fan | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | VU01_S |  |  | 1 | 11000 | 7.6389
KOMF02 | Temp_exhaust_after_heatexchange | The exhaust temperature after the heat exchanger | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TU02 |  |  | 1 | 11000 | 7.6389
KOMF02 | Alarm_filter_exhaust | Alarm at the intake air filter | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | PFU01_F |  |  | 1 | 11000 | 7.6389
KOMF02 | Damper_exhaust | Damper for the exhaust | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | SMU01_K |  |  | 1 | 11000 | 7.6389
KOMF02 | Temp_exhaust | Temperature from the exhaust before heat exchanger | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TU01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Exhaust_pressure | Pressure in the exhaust air | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | PTU01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Heat_exchanger_efficiency | Efficiency of the heat exchanger | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | VIRKNINGSGRAD |  |  | 1 | 11000 | 7.6389
KOMF02 | Damper_intake | Damper for the intake | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | SMI01_K |  |  | 1 | 11000 | 7.6389
KOMF02 | Alarm_filter_intake | Alarm for the pressure drop across the filter | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | PFI_01_F |  |  | 1 | 11000 | 7.6389
KOMF02 | Temp_intake | The temperature before the heat exchanger for the intake | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI03 |  |  | 1 | 11000 | 7.6389
KOMF02 | Heat_exchanger_speed | The control signal for the rotating heat exchanger | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | RV01_S |  |  | 1 | 11000 | 7.6389
KOMF02 | Temp_before_heat_coil | The temperature before the heating coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI02 |  |  | 1 | 11000 | 7.6389
KOMF02 | Temp_return_heat_coil | The return temperature inside the heating coil circuit | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TR01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Motor_valve_heat_coil | Signal for the control valve on the heating coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | MVV01_S |  |  | 1 | 11000 | 7.6389
KOMF02 | Energy_heat_coil | The amount of energy from the heating coil to the ventilation system | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | nvoPowerV1 |  |  | 1 | 11000 | 7.6389
KOMF02 | Heat_coil_pump | Status of the pump for the heating coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | PV01_K |  |  | 1 | 11000 | 7.6389
KOMF02 | Temp_supply_heat_coil | The supply temperature inside the heating coil circuit | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TF01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Heat_coil_alarm | Alarm to avoid ice in the heating coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TFI01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Fan_intake_status | Operation of the intake fan | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | VI01_K |  |  | 1 | 11000 | 7.6389
KOMF02 | Fan_intake_speed | Speed of the intake fan | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | VI01_S |  |  | 1 | 11000 | 7.6389
KOMF02 | Temp_setpoint_inlet | Setpoint for the inlet air | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI01_KALK_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Temp_inlet | The temperature of the inlet air | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Intake_pressure | Pressure in the inlet air | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | PTI01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Total_energy_heat_coil | Total energy for heat coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | nvoE1_HeatV1 |  |  | 1 | 11000 | 7.6389
KOMF02 | Total_volume_heat_coil | Total volume for heat coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | nvoV1_Volume |  |  | 1 | 11000 | 7.6389
KOMF02 | Flow_heat_coil | Flow for the heat coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | nvoV1_Flow |  |  | 1 | 11000 | 7.6389
KOMF02 | Supply_temp_heat_coil | Supply temperature heat coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | nvoTemperature1 |  |  | 1 | 11000 | 7.6389
KOMF02 | Return_temp_heat_coil | Return temperature heat coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | nvoTemperature2 |  |  | 1 | 11000 | 7.6389
KOMF02 | Hour_counter_heating_coil | Hour counter heat coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | nvoHourCount |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_Extended_run_time_ventilation_system | Extended workning time for the ventilation system | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | DT01_FORL_DR_TID_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_status_extended_run_time | status workning extended for the time | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | DT01_FORL_DRIFT |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_supply_temperature | Setpoint inlet temperature | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI01_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_desired_room_temperature | Setpoint for room temperature | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TRU01_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_max_inlet_temp | Setpoint for max inlet temperature | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI01_KALK_TRU_MAX_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_min_inlet_temp | Setpoint for min inlet temperature | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI01_KALK_TRU_MIN_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_desired_outlet_temp | Setpoint for inlet temperature based on outlet temp | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TU01_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_max_outlet_temp | Setpoint for max inlet temperature | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI01_KALK_TU_MAX_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_min_outlet_temp | Setpoint for min inlet temperature | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI01_KALK_TU_MIN_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_cooling_recovery_active_setpoint | Setpoint for activating the cooling recovery | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | KØLG_DIFF_T_AKT_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_cooling_recovery_inactive_setpoint | Setpoint for deactivating the cooling recovery | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | KØLG_DIFF_T_DEAKT_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_night_cooling_room_temp | Setpoint for night cooling based on room temp | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | NATKØL_SV_TRU01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_night_cooling_room_temp_outdoor_temp | Setpoint for night cooling based on room temp and outdoor temp | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | NATKØL_SV_LAV_TUD01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_night_cooling_when_outdoor_temp_below_room_temp | Setpoint for night cooling when outdoor temp < room temp | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | NATKØL_SV_D_TUD_TRU |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_max_time_night_cooling | max workning time for the night cooling mode | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | NATKØL_SV_TIM_START |  |  | 1 | 11000 | 7.6389
KOMF02 | Temperature_room_1.104 | Temperature for room 1.104 | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | 1104_TRU01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Temperature_room_1.218 | Temperature for room 1.218 | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | 1218_TRU01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Temperature_room_1.316 | Temperature for room 1.316 | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | 1316_TRU01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_night_heating | Setpoint for night heating | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | NATVARME_SV_TRU01 |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_max_time_night_heating | max workning time for the night heating mode | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | NATVAR_SV_TIM_START |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_winther_start_up_temp | Setpoint for winther start up | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TI01_REG__SV_LAV_UT |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_min_return_temp_heating_coil | Setpoint for min return temp for heating coil | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | TR01_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_inlet_pressure | Setpoint inlet pressure | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | PTI01_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Setting_outlet_pressure | Setpoint outlet pressure | /TM023_0_20_1.011/KOMF02 |  | CHART_KOMF02 | /TM023_0_20_1.011/KOMF02 | PTU01_SV |  |  | 1 | 11000 | 7.6389
KOMF02 | Exhaust_flow |  | /TM023_0_20_1.011/KOMF02 |  |  |  | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h
KOMF02 | Pressure_diff_fan |  | /TM023_0_20_1.011/KOMF02 |  |  |  | SXW_VEN_Rotorveksler_000K/PDU01
KOMF02 | Air_flow_supply |  | /TM023_0_20_1.011/KOMF02 |  |  |  | VI01_FLOW_m3_h
KOMF02 | Pressure_diff_fan_supply |  | /TM023_0_20_1.011/KOMF02 |  |  |  | PDI01
KOMF02 | SEL_value |  | /TM023_0_20_1.011/KOMF02 |  |  |  | SEL_VÆRDI_J_m3
KOMF03 | HC_effect_KOMF03 | Current output effect of the heating coil | /TM023_0_20_1.011/Lon/Net/KOMF03-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | power_f (energymeter)
KOMF03 | HC_energy_accumulated_KOMF03 | Accumulated energy use for the heating coil | /TM023_0_20_1.011/Lon/Net/KOMF03-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | elec_whr_f (energymeter)
KOMF03 | HC_flow_KOMF03 | Flow over the heating coil (does not account for the recirculated flow) | /TM023_0_20_1.011/Lon/Net/KOMF03-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | flow_f (energymeter)
KOMF03 | HC_operation_hours_accumulated_KOMF03 | Accumulated hours in operation for the heating coil | /TM023_0_20_1.011/Lon/Net/KOMF03-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | count_f (energymeter)
KOMF03 | HC_return_temperature_KOMF03 | Temperature of the heating coil water after the HC | /TM023_0_20_1.011/Lon/Net/KOMF03-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | TR01
KOMF03 | HC_supply_temperature_KOMF03 | Temperature of the heating coil water before the HC | /TM023_0_20_1.011/Lon/Net/KOMF03-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | TF01
KOMF03 | HC_volume_accumulated_KOMF03 | Accumulated flow through the heating coil | /TM023_0_20_1.011/Lon/Net/KOMF03-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | vol_f (energymeter)
KOMF03 | Energi_frequency_KOMF03 | Frequency for the electricity meter for the ventilation system | /TM023_0_20_1.011/Lon/Net/KOMF03-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoFrequency
KOMF03 | Energi_average_voltage_KOMF03 | Voltage for the electricity meter for the ventilation system | /TM023_0_20_1.011/Lon/Net/KOMF03-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoVoltsLLAvg
KOMF03 | Energi_Current_phase_L1_KOMF03 | Energi of eletrick current of phase 1 | /TM023_0_20_1.011/Lon/Net/KOMF03-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoCurrentPh1
KOMF03 | Energi_Current_phase_L2_KOMF03 | Energi of eletrick current of phase 2 | /TM023_0_20_1.011/Lon/Net/KOMF03-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoCurrentPh2
KOMF03 | Energi_Current_phase_L3_KOMF03 | Energi of eletrick current of phase 3 | /TM023_0_20_1.011/Lon/Net/KOMF03-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoCurrentPh3
KOMF03 | Energi_Total_power_KOMF03 | Total power for the electricity meter for the ventilation system | /TM023_0_20_1.011/Lon/Net/KOMF03-EM01/EnergyMeter/RMSMeas [20001] |  |  |  | nvoActPowerSum
KOMF03 | Energi_Total energy_KOMF03 | Total energy for the electricity meter for the ventilation system | /TM023_0_20_1.011/Lon/Net/KOMF03-EM01/EnergyMeter/EnergyMeas [1] |  |  |  | nvoTotkWhImp
KOMF03 | Energi_Total_reactivie_energy_KOMF03 | Total reactive energy for the electricity meter for the ventilation system | /TM023_0_20_1.011/Lon/Net/KOMF03-EM01/EnergyMeter/EnergyMeas [1] |  |  |  | nvoTotkVARhImp
KØ01 | Supply_temp_consumer | Temperature for the supply to the consumer | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØTT01Value |  |  | 1 | 11000 | 7.6389
KØ01 | Supply_temp_setpoint | Setpoint for the supply temperature for the consumer | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØTT01_Kurve_SP |  |  | 1 | 11000 | 7.6389
KØ01 | Supply_pressure_consumer | The pressure in the supply pipe | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØPT_02_kPa |  |  | 1 | 11000 | 7.6389
KØ01 | Supply_flow_consumer | The flow in the supply pipe | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | 302 VolumeFlow |  |  | 1 | 11000 | 7.6389
KØ01 | Supply_pump_setpoint | The pump in the supply pipe | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | 104 setpoint |  |  | 1 | 11000 | 7.6389
KØ01 | Temperature_out_buffer_tank | The temperature out of the buffer tank | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØTT07 |  |  | 1 | 11000 | 7.6389
KØ01 | Temperature_in_buffer_tank | The temperature into the buffer tank | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØTT06 |  |  | 1 | 11000 | 7.6389
KØ01 | Expansion_tank_pressure | The pressure in the buffer tank | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØPT03 |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_temp_out | The temperature out of the cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | TEMP UD AF MASKINE |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_power_out | The power produced by the cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK02 |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_total_energy | The total energy of the cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK02 |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_total_volume | The total volume of the cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK02 |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_total_flow | The flow out of the cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK02 |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_supply_temp | The supply temp from cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK02 |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_return_temp | The return temp from cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK02 |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_hour_counter | The hour counter of the cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK02 |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_fan_exhaust | Exhaust fan from the cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | US20 |  |  | 1 | 11000 | 7.6389
KØ01 | Return_temp_consumer | Return temperature from the consumer | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØTT03 |  |  | 1 | 11000 | 7.6389
KØ01 | Return_pump_ON_OFF | ON-Off control for the return pump of the consumer | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP03 |  |  | 1 | 11000 | 7.6389
KØ01 | Return_pump_level_activity | The activity level of the return pump | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP03_S |  |  | 1 | 11000 | 7.6389
KØ01 | Return_pump_rotation_speed | The rotation speed of the return pump | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | FE90 |  |  | 1 | 11000 | 7.6389
KØ01 | Motor_valve_return | The motor valve on the return pipe from consumer | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØMV03_P |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_temp_in | The cooling machine of the temp in | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | TEMP IND I MASKINE |  |  | 1 | 11000 | 7.6389
KØ01 | Motor_valve_return_setpoint | The temperature into the cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØMV03 |  |  | 1 | 11000 | 7.6389
KØ01 | Heat_exchanger_total_energy | Total energy produced from heat exchanger from energy meter | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK01 |  |  | 1 | 11000 | 7.6389
KØ01 | Heat_exchanger_total_volume | Total volume from heat exchanger from energy meter | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK01 |  |  | 1 | 11000 | 7.6389
KØ01 | Heat_exchanger_power | Power from heat exchanger from energy meter | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK01 |  |  | 1 | 11000 | 7.6389
KØ01 | Heat_exchanger_flow | Flow from heat exchanger from energy meter | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK01 |  |  | 1 | 11000 | 7.6389
KØ01 | Heat_exchanger_supply_temp | The supply temp of the heat exchanger from energy meter | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK01 |  |  | 1 | 11000 | 7.6389
KØ01 | Heat_exchanger_return_temp | The heat exchanger of the return temp from energy meter | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK01 |  |  | 1 | 11000 | 7.6389
KØ01 | Heat_exchanger_hour_counter | The heat exchanger of the hour counter from energy meter | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | QMK01 |  |  | 1 | 11000 | 7.6389
KØ01 | Cooling_machine_operational_hours | The operational hours of the cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØKM01_Drifttimer |  |  | 1 | 11000 | 7.6389
KØ01 | Supply_temp_heat_exhanger_consumer_side | The supply temp heat exhanger of the consumer side | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØTT05 |  |  | 1 | 11000 | 7.6389
KØ01 | Motor_valve_return_heat_exchanger_consumer_side | The motor valve on the return to the heat exchanger | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØL01-KØMV04_P |  |  | 1 | 11000 | 7.6389
KØ01 | Motor_valve_return_setpoint_heat_exchanger_consumer_side | The setpoint of the motor valve on the return to the heat exchanger | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØMV04 |  |  | 1 | 11000 | 7.6389
KØ01 | Motor_valve_supply_heat_exchanger_production_side | The motor valve on the production side to the heat exchanger | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØL01-KØMV02_P |  |  | 1 | 11000 | 7.6389
KØ01 | Motor_valve_setpoint_supply_heat_exchanger_production_side | The setpoint of the motor valve on the production side to the heat exchanger | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØMV02 |  |  | 1 | 11000 | 7.6389
KØ01 | Motor_valve_production_side_cooling_machine | The motor valve close to the cooling compressor on the production side | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØL01-KØMV01_P |  |  | 1 | 11000 | 7.6389
KØ01 | Motor_valve_setpoint_production_side_cooling_machine | The setpoint of the motor valve close to the cooling compressor on the production side | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØMV01 |  |  | 1 | 11000 | 7.6389
KØ01 | Pressure_air_dry_cooler_supply | The pressure on the pump close to the air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØPT_01_kPa |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_air_dry_cooler_ON_OFF | ON-Off control for the pump close to the air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP01 |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_air_dry_cooler_level_activity | level of activity for the pump close to the air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP01_S |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_air_dry_cooler_flow | The flow of the pump close to the air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | 304 Speed |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_air_dry_cooler_rotation_speed | The rotation speed of the pump close to the air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | 302 Speed |  |  | 1 | 11000 | 7.6389
KØ01 | Expansion_tank_pressure_air_dry_cooler | The pressure of the expansion tank close to the air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØPT04 |  |  | 1 | 11000 | 7.6389
KØ01 | Temperature_out_air_dry_cooler | Temperature out of the air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØL01-KØTT02 |  |  | 1 | 11000 | 7.6389
KØ01 | Temperature_in_air_dry_cooler | Temperature into the air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØL01-KØTT04 |  |  | 1 | 11000 | 7.6389
KØ01 | Air_dry_cooler_control_signal | The control signal of the air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØTK01_S |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_consumer_ON_OFF | ON/OFF for the pump supplying the consumer | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP02 |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_consumer_level_activity | The level of activity of the pump supplying the consumer | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP02_S |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_consumer_level_activity_setpoint | The setpoint of level of activity for the pump supplying the consumer | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP02_SV |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_return_consumer_setpoint_when_cooling_compressing | The setpoint of the return pump for the consumer when running with cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP03_SV_Maskinkøl |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_return_consumer_setpoint_when_free_cooling | The setpoint of the return pump for the consumer when running with free cooling | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP03_SV_Frikøl |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_air_dry_cooler_setpoint_when_cooling_compressing | The setpoint of the pump close to the air dry cooler when running with cooling compressor | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP01_SV_Maskinkøl |  |  | 1 | 11000 | 7.6389
KØ01 | Pump_air_dry_cooler_setpoint_when_free_cooling | The setpoint of the pump close to the air dry cooler when running with free cooling | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØP01_SV_Frikøl |  |  | 1 | 11000 | 7.6389
KØ01 | Temperature_air_dry_cooler_setpoint_when_cooling_compressing | The temperature setpoint for air dry cooler when cooling compressing | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | KØTT02_SV_Maskin |  |  | 1 | 11000 | 7.6389
KØ01 | Temperature_setpoint_switch_free_cooling_and_cooling_compressing | The temperature switchpoint for air dry cooler | /TM023_1_20_1031B |  | CHART_KØ01 | /TM023_1_20_1031B | SV_S_V_SKIFT |  |  | 1 | 11000 | 7.6389
KØ01 | Power_air_dry_cooler_and_circulation_pump | Power consumption of the air dry cooler and the pumps | /TM023_0_20_1121 |  | CHART_KØ01 | /TM023_1_20_1031B | nvoActPowerSum |  |  | 1 | 11000 | 7.6389
KØ01 | Total_energy_air_dry_cooler_circulation_pump | Total energy consumption of the air dry cooler and the pumps | /TM023_0_20_1121 |  | CHART_KØ01 | /TM023_1_20_1031B | nvoTotkWhlmp |  |  | 1 | 11000 | 7.6389
LAB01_QMK01 Energi | LAB01_QMK01 Energi | Kølevand ventilation LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Energi | LAB01_QMK01 Energi | Kølevand ventilation LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Flow | LAB01_QMK01 Flow | Kølevand ventilation LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Flow | LAB01_QMK01 Flow | Kølevand ventilation LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Frem temp | LAB01_QMK01 Frem temp | Kølevand ventilation LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Frem temp | LAB01_QMK01 Frem temp | Kølevand ventilation LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Retur temp | LAB01_QMK01 Retur temp | Kølevand ventilation LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Retur temp | LAB01_QMK01 Retur temp | Kølevand ventilation LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Timer | LAB01_QMK01 Timer | Kølevand ventilation LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Timer | LAB01_QMK01 Timer | Kølevand ventilation LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Volumen | LAB01_QMK01 Volumen | Kølevand ventilation LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMK01 Volumen | LAB01_QMK01 Volumen | Kølevand ventilation LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMK01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
LAB01_QMV01 | Space_heating_LAB01_energy | District heating accumulated energy supplied for LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoE1_HeatV1
LAB01_QMV01 | Space_heating_LAB01_volume | District heating accumulated volume supplied for LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Volume
LAB01_QMV01 | Space_heating_LAB01_power | District heating power currently supplied to LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoPowerV1
LAB01_QMV01 | Space_heating_LAB01_flow | District heating flow currently supplied to LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Flow
LAB01_QMV01 | Space_heating_LAB01_supply_temperature | District heating supply temperature currently supplied to LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature1
LAB01_QMV01 | Space_heating_LAB01_return_temperature | District heating return temperature currently supplied from LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature2
LAB01_QMV01 | Space_heating_LAB01_operation_hours | District heating accumulated number of operation hours for LAB01 | /TM023_0_21_1125/Lon/Net/LAB01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoHourCount
LAB02_QMV01 | Space_heating_LAB02_energy | District heating accumulated energy supplied for LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoE1_HeatV1
LAB02_QMV01 | Space_heating_LAB02_volume | District heating accumulated volume supplied for LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Volume
LAB02_QMV01 | Space_heating_LAB02_power | District heating power currently supplied to LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoPowerV1
LAB02_QMV01 | Space_heating_LAB02_flow | District heating flow currently supplied to LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoV1_Flow
LAB02_QMV01 | Space_heating_LAB02_supply_temperature | District heating supply temperature currently supplied to LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature1
LAB02_QMV01 | Space_heating_LAB02_return_temperature | District heating return temperature currently supplied from LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoTemperature2
LAB02_QMV01 | Space_heating_LAB02_operation_hours | District heating accumulated number of operation hours for LAB02 | /TM023_0_20_1110/Lon/Net/LAB02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0] |  |  |  | nvoHourCount
P-Fund_QMV01 Aktuel Effekt | P-Fund_QMV01 Aktuel Effekt | Fjernvarme ventilation P_Fund | /TM023_0_21_1101/Lon/Net/P-Fund_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Fund_QMV01 Energi | P-Fund_QMV01 Energi | Fjernvarme ventilation P_Fund | /TM023_0_21_1101/Lon/Net/P-Fund_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Fund_QMV01 Flow | P-Fund_QMV01 Flow | Fjernvarme ventilation P_Fund | /TM023_0_21_1101/Lon/Net/P-Fund_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Fund_QMV01 Frem temp | P-Fund_QMV01 Frem temp | Fjernvarme ventilation P_Fund | /TM023_0_21_1101/Lon/Net/P-Fund_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Fund_QMV01 Retur temp | P-Fund_QMV01 Retur temp | Fjernvarme ventilation P_Fund | /TM023_0_21_1101/Lon/Net/P-Fund_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Fund_QMV01 Timer | P-Fund_QMV01 Timer | Fjernvarme ventilation P_Fund | /TM023_0_21_1101/Lon/Net/P-Fund_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Fund_QMV01 Volumen | P-Fund_QMV01 Volumen | Fjernvarme ventilation P_Fund | /TM023_0_21_1101/Lon/Net/P-Fund_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-klima | Electricity_meter_frequency | Frequency for the electricity meter for the ventilation system | /TM023_1_20_1101/Lon/Net/UT01-2-C53.1/EnergyMeter63A |  | CHART_P_KLIMA | /TM023_0_22_1166 | ELM_frequency |  |  | 1 | 11000 | 7.6389
P-klima | Electricity_meter_average_voltage | Voltage for the electricity meter for the ventilation system | /TM023_1_20_1101/Lon/Net/UT01-2-C53.1/EnergyMeter63A |  | CHART_P_KLIMA | /TM023_0_22_1167 | ELM_average_voltage |  |  | 1 | 11000 | 7.6389
P-klima | Electricity_meter_total_power | Total power for the electricity meter for the ventilation system | /TM023_1_20_1101/Lon/Net/UT01-2-C53.1/EnergyMeter63A |  | CHART_P_KLIMA | /TM023_0_22_1168 | ELM_total_power |  |  | 1 | 11000 | 7.6389
P-klima | Electricity_meter_total_energy | Total energy for the electricity meter for the ventilation system | /TM023_1_20_1101/Lon/Net/UT01-2-C53.1/EnergyMeter63A |  | CHART_P_KLIMA | /TM023_0_22_1169 | ELM_total_energy |  |  | 1 | 11000 | 7.6389
P-klima | Electricity_meter_total_reactive_energy | Total reactive energy for the electricity meter for the ventilation system | /TM023_1_20_1101/Lon/Net/UT01-2-C53.1/EnergyMeter63A |  | CHART_P_KLIMA | /TM023_0_22_1170 | ELM_reactive_energy |  |  | 1 | 11000 | 7.6389
P-klima | Pump_heating_coil | Ciiculation pump for the heating coil | /TM023_0_22_1125/P-Klima |  | CHART_P_KLIMA | /TM023_0_22_1148 | PV01_K |  |  | 1 | 11000 | 7.6389
P-klima | Operation_status_rotary_exchanger | Status of the rotary ventilation system in P-klima | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1125 | Drift |  |  | 1 | 11000 | 7.6389
P-klima | Exhaust_damper_SMU01 | Position of the exhaust damper | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1126 | SMU01_K |  |  | 1 | 11000 | 7.6389
P-klima | Exhaust_ventilation_unit_control_signal | Control signal for exhaust ventilaiton unit | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1127 | VU01_S |  |  | 1 | 11000 | 7.6389
P-klima | Exhaust_ventilation_unit_ON-OFF | Tells if the exhaust ventilaiton unit is on/off | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1128 | VU01_K |  |  | 1 | 11000 | 7.6389
P-klima | Exhaust_temperature | Temperature of the exhaust | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1129 | TU02 |  |  | 1 | 11000 | 7.6389
P-klima | Exhaust_filter_alarm | Alarm for the filter at the exhaust | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1130 | PFU01 |  |  | 1 | 11000 | 7.6389
P-klima | Exhaust_temperature_before_heat_exchanger | The temperature of the exhaust before the heat exchanger | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1131 | TU01 |  |  | 1 | 11000 | 7.6389
P-klima | Exhaust_pressure | The pressure at the exhaust | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1132 | PTU01 |  |  | 1 | 11000 | 7.6389
P-klima | Heat_exchanger_efficiency | The efficiency of the heat exchanger | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1133 | VIRKNINGSGRAD |  |  | 1 | 11000 | 7.6389
P-klima | Intake_damper_SMI01 | Position of the intake damper | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1134 | SMI01_K |  |  | 1 | 11000 | 7.6389
P-klima | Intake_temperature | Temperature of the intake | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1135 | TI03 |  |  | 1 | 11000 | 7.6389
P-klima | Rotary_heat_exchanger_control_signal | Control signal for the rotary heat exchanger | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1136 | RV01_S |  |  | 1 | 11000 | 7.6389
P-klima | Intake_temperature_after_heat_exchanger | Temperature after the rotary heat exchanger | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1137 | TI02 |  |  | 1 | 11000 | 7.6389
P-klima | Alarm_intake_filter | Alarm for the filter at the intake | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1138 | PFI01_F |  |  | 1 | 11000 | 7.6389
P-klima | Intake_ventilation_unit_on-off | Tells if the intake ventilaiton unit is on/off | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1139 | VI01_K |  |  | 1 | 11000 | 7.6389
P-klima | Intake_ventilation_unit_control_signal | Control signal for the intake ventilation unit | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1140 | VI01_S |  |  | 1 | 11000 | 7.6389
P-klima | Temperature_sensor_frost | Temperature sensor for frost | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1141 | TFI01 |  |  | 1 | 11000 | 7.6389
P-klima | Temperature_sensor_between_heating_cooling | Temperature sensor between the heating and cooling coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1142 | TI04 |  |  | 1 | 11000 | 7.6389
P-klima | Intake_temperature_calculated_temperature_setpoint | The calculated setpoint to reach for inlet air | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1143 | TI01_KALK_SV |  |  | 1 | 11000 | 7.6389
P-klima | Intake_temperature_after_coils | The measured inlet temperature for the air | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1144 | TI01 |  |  | 1 | 11000 | 7.6389
P-klima | Inlet_pressure | The pressure at the inlet | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1145 | PTI01 |  |  | 1 | 11000 | 7.6389
P-klima | Temperature_heating_coil_return | Return temperature for the heating coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1146 | TR01 |  |  | 1 | 11000 | 7.6389
P-klima | Temperature_heating_coil_supply | Supply temperature for heating coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1147 | TF01 |  |  | 1 | 11000 | 7.6389
P-klima | Motor_valve_heating_coil | Signal for the control valve on the heating coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1149 | MVV01_S |  |  | 1 | 11000 | 7.6389
P-klima | Accumulated_energy_heating_coil | Accumulated energy for the heating coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1150 | QMV01_Energi |  |  | 1 | 11000 | 7.6389
P-klima | Volume_heating_coil | Total volume for the heating coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1151 | QMV01_Volumen |  |  | 1 | 11000 | 7.6389
P-klima | Power_heating_coil | Power heating coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1152 | QMV01_effekt |  |  | 1 | 11000 | 7.6389
P-klima | Flow_heating_coil | Flow to the heating coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1153 | QMV01_flow |  |  | 1 | 11000 | 7.6389
P-klima | Supply_temperature_heating_coil_before_mixing_shunt | Supply temperature for heating coil before the mixing shunt | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1154 | QMV01_Frem |  |  | 1 | 11000 | 7.6389
P-klima | Return_temperature_heating_coil_after_mixing_shunt | Return temperature for the heating coil after the mixing shunt | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1155 | QMV01_Retur |  |  | 1 | 11000 | 7.6389
P-klima | Hour_counter_heating_coil | Hour counter for the heating coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1156 | QMV01_time |  |  | 1 | 11000 | 7.6389
P-klima | Pump_cooling_coil | Circulation pump for the cooling coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1157 | PK01_K |  |  | 1 | 11000 | 7.6389
P-klima | Motor_valve_cooling_coil | Motor valve for the cooling coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1158 | MVK01_S |  |  | 1 | 11000 | 7.6389
P-klima | Accumulated_energy_cooling_coil | Accumulated energy for the cooling coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1159 | QMK01_Energi |  |  | 1 | 11000 | 7.6389
P-klima | Volume_cooling_coil | Total volume for the cooling coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1160 | QMK01_Volumen |  |  | 1 | 11000 | 7.6389
P-klima | Power_cooling_coil | Power cooling coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1161 | QMK01_effekt |  |  | 1 | 11000 | 7.6389
P-klima | Flow_cooling_coil | Flow to the cooling coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1162 | QMK01_flow |  |  | 1 | 11000 | 7.6389
P-klima | Supply_temperature_cooling_coil | Supply temperature for cooling coil before the mixing shunt | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1163 | QMK01_Frem |  |  | 1 | 11000 | 7.6389
P-klima | Return_temperature_cooling_coil | Return temperature for the cooling coil after the mixing shunt | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1164 | QMK01_Retur |  |  | 1 | 11000 | 7.6389
P-klima | Hour_counter_cooling_coil | Hour counter for the cooling coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1165 | QMK01_time |  |  | 1 | 11000 | 7.6389
P-klima | Software_reverser | For the main station | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1171 | Omskifter_hovedstation |  |  | 1 | 11000 | 7.6389
P-klima | Hardware_reverser | For the main station | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1172 | Omskifter_tavlefront |  |  | 1 | 11000 | 7.6389
P-klima | Setting_ventilation_system_extended_working_time | Extended workning time for the ventilation system | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1173 | FORL_DRIFT |  |  | 1 | 11000 | 7.6389
P-klima | Setting_fixed_inlet_temperature | Setting for the inlet temperature of the ventilation system based on room temperature | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1174 | TI01_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_desired_room_temperature | Setting for the desired room temperature | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1175 | TRU01_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_max_inlet_temperature | Maximun inlet temperature for the ventilation system based on room temperature | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1176 | TI01_KALK_TRU_MAX_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_minimum_inlet_temperature | Minimum inlet temperature for the ventilation system based on room temperature | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1177 | TI01_KALK_TRU_MIN_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_desired_outlet_temperature | Setting for the desired inlet temperature based on outlet temperature | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1178 | TU01_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_max_inlet_temperature_based_on_outlet | Maximun inlet temperature for the ventilation system based on outlet temperautre | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1179 | TI01_KALK_TU_MAX_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_min_inlet_temperature_based_on_outlet | Minimum inlet temperature for the ventilation system based on outlet temperature | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1180 | TI01_KAlK_TU_MIN_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_setpoint_cooling_recovery | Setpoint for activating the cooling recovery | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1181 | KØLG_DIFF_T_AKT_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_setpoint_deactivation_cooling_recovery | Setpoint for deactivating the cooling recovery | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1182 | KØLG_DIFF_T_DEAKT_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_night_cooling_when_room_temperature | Setpoint for night cooling based on room temp | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1183 | NATKØL_SV_TRU01 |  |  | 1 | 11000 | 7.6389
P-klima | Setting_night_cooling_when_outdoor_temperature | Setpoint for night cooling based on room temp and outdoor temp | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1184 | NATKØL_SV_LAV_TUD01 |  |  | 1 | 11000 | 7.6389
P-klima | Setting_night_cooling_when_outdoor_lower_than_room_temperature | Setpoint for night cooling when outdoor temp < room temp | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1185 | NATKØL_SV_D_TUD_TRU |  |  | 1 | 11000 | 7.6389
P-klima | Setting_max_time_night_cooling | max workning time for the night cooling mode | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1186 | NATKØL_SV_TIM_START |  |  | 1 | 11000 | 7.6389
P-klima | Setting_room_temperature_reference_room | Setpoint for the room temperature of the referece room | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1187 | TRU01 |  |  | 1 | 11000 | 7.6389
P-klima | Setting_night_heating_setpoint | Setpoint for night heating | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1188 | NATVARME_SV_TRU01 |  |  | 1 | 11000 | 7.6389
P-klima | Setting_max_time_night_heating | max workning time for the night heating mode | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1189 | NATVAR_SV_TIM_START |  |  | 1 | 11000 | 7.6389
P-klima | Setting_setpoint_winter_start_up | Setpoint for when to do a winter start up | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1190 | TI01_REG__SV_LAV_UT |  |  | 1 | 11000 | 7.6389
P-klima | Setting_minimum_return_temp_heating_coil | Setpoint for minimum return temperature from heating coil | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1191 | TR01_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_desired_inlet_air_pressure | Setpoint for desired air pressure in inlet | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1192 | PTI01_SV |  |  | 1 | 11000 | 7.6389
P-klima | Setting_desired_outlet_air_pressure | Setpoint for desired air pressure in outlet | /TM023_0_22_1125 |  | CHART_P_KLIMA | /TM023_0_22_1193 | PTU01_SV |  |  | 1 | 11000 | 7.6389
P-Vand_QMV01 Aktuel Effekt | P-Vand_QMV01 Aktuel Effekt | Fjernvarme ventilation P_Vand | /TM023_0_24_1125/Lon/Net/P-Vand_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Vand_QMV01 Energi | P-Vand_QMV01 Energi | Fjernvarme ventilation P_Vand | /TM023_0_24_1125/Lon/Net/P-Vand_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Vand_QMV01 Flow | P-Vand_QMV01 Flow | Fjernvarme ventilation P_Vand | /TM023_0_24_1125/Lon/Net/P-Vand_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Vand_QMV01 Frem temp | P-Vand_QMV01 Frem temp | Fjernvarme ventilation P_Vand | /TM023_0_24_1125/Lon/Net/P-Vand_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Vand_QMV01 Retur temp | P-Vand_QMV01 Retur temp | Fjernvarme ventilation P_Vand | /TM023_0_24_1125/Lon/Net/P-Vand_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Vand_QMV01 Timer | P-Vand_QMV01 Timer | Fjernvarme ventilation P_Vand | /TM023_0_24_1125/Lon/Net/P-Vand_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Vand_QMV01 Volumen | P-Vand_QMV01 Volumen | Fjernvarme ventilation P_Vand | /TM023_0_24_1125/Lon/Net/P-Vand_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Værk_QMV01 Aktuel Effekt | P-Værk_QMV01 Aktuel Effekt | Fjernvarme ventilation P_Værk | /TM023_0_25_1125/Lon/Net/P-Værk_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Værk_QMV01 Energi | P-Værk_QMV01 Energi | Fjernvarme ventilation P_Værk | /TM023_0_25_1125/Lon/Net/P-Værk_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Værk_QMV01 Flow | P-Værk_QMV01 Flow | Fjernvarme ventilation P_Værk | /TM023_0_25_1125/Lon/Net/P-Værk_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Værk_QMV01 Frem temp | P-Værk_QMV01 Frem temp | Fjernvarme ventilation P_Værk | /TM023_0_25_1125/Lon/Net/P-Værk_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Værk_QMV01 Retur temp | P-Værk_QMV01 Retur temp | Fjernvarme ventilation P_Værk | /TM023_0_25_1125/Lon/Net/P-Værk_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Værk_QMV01 Timer | P-Værk_QMV01 Timer | Fjernvarme ventilation P_Værk | /TM023_0_25_1125/Lon/Net/P-Værk_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
P-Værk_QMV01 Volumen | P-Værk_QMV01 Volumen | Fjernvarme ventilation P_Værk | /TM023_0_25_1125/Lon/Net/P-Værk_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]
R.1.001 | PIR_Activity_1.001 | If the room is considered active | /TM023_1_20_1103/R 1.001
R.1.001 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_1_20_1103/Lon/Net/Rum 1.001_STR
R.1.001 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_1_20_1103/Lon/Net/Rum 1.001_STR
R.1.001 | LYS01 on | ON/OFF of the light | /TM023_1_20_1103/R 1.001/Logninger
R.1.001 | LYS01 niveau | Light level setpoint | /TM023_1_20_1103/R 1.001/Logninger
R.1.001 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_1_20_1103/Lon/Net/CTS102
R.1.001 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_1_20_1103/R 1.001
R.1.001A | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Lux_level_ceiling | Light level measured in the ceiling | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Light_ON_OFF | ON/OFF of the light | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Light_level_room | Light level setpoint | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | CO2_level | Current measured CO2 level in the room | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Temperature_global_setpoint | Global temperature setpoint | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Room_temp_deadband_day | Deadband during daytime | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Room_temp_deadband_standby | Deadband during standby | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Room_temp_deadband_night | Deadband during nighttime | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Heating_valve_1.001A | Opening signal of the radiator valve | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Temperature_heating_setpoint_1.001A | Lower limit for activating heating | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Temperature_cooling_setpoint_1.001A | Upper limit for activating cooling | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | PIR_Activity_1.001A | If the room is considered active | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | Point_extraction | If the point extraction is active | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.001A | VAV_opening_if_point_extraction | VAV opening if the point extraction is active | /TM023_1_20_1103/Lon/Net/Rum 1.001A
R.1.006 | PIR_Activity_1.006 | If the room is considered active | /TM023_1_20_1103/Lon/Net/Rum 1.006 |  |  |  | ZoneAktiv |  |  | 1 | 11000 | 7.6389 | 0
R.1.006 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Light_ON_OFF | ON/OFF of the light | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Light_level_room | Light level setpoint | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | indoor_temp_room_1.006 | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_1_20_1103/Lon/Net
R.1.006 | CO2_room_1.006 | Current measured CO2 level in the room | /TM023_1_20_1103/Lon/Net
R.1.006 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Temperature_global_setpoint | Global temperature setpoint | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Room_temp_deadband_day | Deadband during daytime | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Room_temp_deadband_standby | Deadband during standby | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Room_temp_deadband_night | Deadband during nighttime | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Heating_valve_1.006 | Opening signal of the radiator valve | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | setpoint_temp_room_1.006 | Lower limit for activating heating | /TM023_1_20_1103/Lon/Net
R.1.006 | Temperature_cooling_setpoint_1.006 | Upper limit for activating cooling | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.006 | Vindue_1.006 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_1_20_1103/Lon/Net/Rum 1.006
R.1.010 | PIR_Activity_1.010 | If the room is considered active | /TM023_1_20_1103/Lon/Net/Rum 1.010 |  |  |  | ZoneAktiv |  |  | 1 | 11000 | 7.6389 | 1
R.1.010 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Light_ON_OFF | ON/OFF of the light | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Light_level_room | Light level setpoint | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | indoor_temp_room_1.010 | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_1_20_1103/Lon/Net
R.1.010 | CO2_room_1.010 | Current measured CO2 level in the room | /TM023_1_20_1103/Lon/Net
R.1.010 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | setpoint_temp_room_1.010 | Global temperature setpoint | /TM023_1_20_1103/Lon/Net
R.1.010 | Room_temp_deadband_day | Deadband during daytime | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Room_temp_deadband_standby | Deadband during standby | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Room_temp_deadband_night | Deadband during nighttime | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Heating_valve_1.010 | Opening signal of the radiator valve | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Temperature_heating_setpoint_1.010 | Lower limit for activating heating | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Temperature_cooling_setpoint_1.010 | Upper limit for activating cooling | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Vindue_1.010 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.010 | Ventilation_cooling_valve |  | /TM023_1_20_1103/Lon/Net/Rum 1.010
R.1.011 | Light_ON_OFF | Light ON/OFF | /TM023_1_20_1101/Lon/Net/LDali Klima |  | CHART_R.1.011 | /TM023_1_20_1101 | nvoGPValueFb.Value.state |  |  | 1 | 11000 | 7.6389 | 3
R.1.011 | Light_level | The lightning level in % | /TM023_1_20_1101/Lon/Net/LDali Klima |  | CHART_R.1.011 | /TM023_1_20_1101 | nvoGPValueFb.Value.value |  |  | 1 | 11000 | 7.6389 | 4
R.1.011 | PIR_STAT_01 | ? | /TM023_1_20_1101/Lon/Net/CTS103 |  | CHART_R.1.011 | /TM023_1_20_1101 | PIR_STAT |  |  | 1 | 11000 | 7.6389 | 2
R.1.011 | Room_temperature | Room temperature | /TM023_1_20_1101/Lon/Net |  | CHART_R.1.011 | /TM023_1_20_1101 | nvoSpaceTemp |  |  | 1 | 11000 | 7.6389 | 6
R.1.011 | Offset_STR_Panel | Offset temperature from STR panel | /TM023_1_20_1101/Lon/Net |  | CHART_R.1.011 | /TM023_1_20_1101 | nvoSetptOffset |  |  | 1 | 11000 | 7.6389 | 7
R.1.011 | STATUS_PIR | Activity of PIR | /TM023_1_20_1101 |  | CHART_R.1.011 | /TM023_1_20_1101 | PIR01_STATUS |  |  | 1 | 11000 | 7.6389 | 5
R.1.011 | Setting_run_time_PIR | Run time on PIR | /TM023_1_20_1101 |  | CHART_R.1.011 | /TM023_1_20_1101 | PIR01_OFF |  |  | 1 | 11000 | 7.6389 | 8
R.1.011 | Light_under_deck | If the light underneath the deck is on/off | /TM023_1_20_1101/Lon/Net/CTS103
R.1.015A | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Lux_level_ceiling | Light level measured in the ceiling | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Light_ON_OFF | ON/OFF of the light | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Light_level_room | Light level setpoint | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | CO2_level | Current measured CO2 level in the room | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Temperature_global_setpoint | Global temperature setpoint | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Room_temp_deadband_day | Deadband during daytime | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Room_temp_deadband_standby | Deadband during standby | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Room_temp_deadband_night | Deadband during nighttime | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Heating_valve_1.015A | Opening signal of the radiator valve | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Temperature_heating_setpoint_1.015A | Lower limit for activating heating | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | Temperature_cooling_setpoint_1.015A | Upper limit for activating cooling | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.015A | PIR_Activity_1.015A | If the room is considered active | /TM023_1_20_1101/Lon/Net/Rum 1.015A
R.1.104 | PIR_Activity_1.104 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.104 |  |  |  | ZoneAktiv | [5 empty] | 25
R.1.104 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.104/Logninger
R.1.104 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.104/Logninger
R.1.104 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.104/Logninger
R.1.104 | Temperature_heating_setpoint_1.104 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Temperature_cooling_setpoint_1.104 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Vindue_1.104 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_2_20_1.103B/Lon/Net/Rum 1.104/Logninger
R.1.104 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.104 | Heating_valve_1.104 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.104
R.1.106 | PIR_Activity_1.106 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.106 |  |  |  | ZoneAktiv | [5 empty] | 26
R.1.106 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.106/Logninger
R.1.106 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.106/Logninger
R.1.106 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.106/Logninger
R.1.106 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Vindue_1.106 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_2_20_1.103B/Lon/Net/Rum 1.106/Logninger
R.1.106 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Heating_valve_1.106 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Temperature_cooling_setpoint | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.106 | Temperature_heating_setpoint | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.106
R.1.108 | PIR_Activity_1.108 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.108 |  |  |  | ZoneAktiv | [5 empty] | 27
R.1.108 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.108/Logninger
R.1.108 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.108/Logninger
R.1.108 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.108/Logninger
R.1.108 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Vindue_1.108 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_2_20_1.103B/Lon/Net/Rum 1.108/Logninger
R.1.108 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Heating_valve_1.108 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Temperature_cooling_setpoint | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.108 | Temperature_heating_setpoint | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.108
R.1.110 | PIR_Activity_1.110 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.110 |  |  |  | ZoneAktiv | [5 empty] | 28
R.1.110 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.110/Logninger
R.1.110 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.110/Logninger
R.1.110 | Temperature_heating_setpoint_1.110 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Temperature_cooling_setpoint_1.110 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Ventilation_flow | Ventilation flow | /TM023_2_20_1.103B/Modbus Master Network/LabVent_1_110
R.1.110 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.110 | Heating_valve_1.110 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.110
R.1.114 | PIR_Activity_1.114 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.114 |  |  |  | ZoneAktiv | [5 empty] | 29
R.1.114 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.114/Logninger
R.1.114 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.114/Logninger
R.1.114 | Temperature_heating_setpoint_1.114 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Temperature_cooling_setpoint_1.114 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Ventilation_flow | Ventilation flow | /TM023_2_20_1.103B/Modbus Master Network/LabVent_1_114
R.1.114 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | Heating_valve_1.114 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.114 | CO2_setpoint | CO2 setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.114
R.1.116 | PIR_Activity_1.116 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.116 |  |  |  | ZoneAktiv | [5 empty] | 30
R.1.116 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.116/Logninger
R.1.116 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.116/Logninger
R.1.116 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.116/Logninger
R.1.116 | Temperature_heating_setpoint_1.116 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Temperature_cooling_setpoint_1.116 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Radiator_valve | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | PIR_ceiling | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Lux_meter | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.116
R.1.116 (fancoil 1) | Status | Fancoil speed | /TM023_2_20_1.103B/Modbus Master Network/Fancoil Rum 1.116_1
R.1.116 (fancoil 1) | Temperatur_SP | Fancoil temperature setpoint | /TM023_2_20_1.103B/Modbus Master Network/Fancoil Rum 1.116_1
R.1.116 (fancoil 1) | Temperatur | Fancoil temperature | /TM023_2_20_1.103B/Modbus Master Network/Fancoil Rum 1.116_1
R.1.116 (fancoil 2) | Status | Fancoil speed | /TM023_2_20_1.103B/Modbus Master Network/Fancoil Rum 1.116_2
R.1.116 (fancoil 2) | Temperatur_SP | Fancoil temperature setpoint | /TM023_2_20_1.103B/Modbus Master Network/Fancoil Rum 1.116_2
R.1.116 (fancoil 2) | Temperatur | Fancoil temperature | /TM023_2_20_1.103B/Modbus Master Network/Fancoil Rum 1.116_2
R.1.118 | PIR_Activity_1.118 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.118 |  |  |  | ZoneAktiv | [5 empty] | 31
R.1.118 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.118/Logninger
R.1.118 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.118/Logninger
R.1.118 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.118/Logninger
R.1.118 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Vindue_1.118 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Heating_valve_1.118 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Temperature_heating_setpoint_1.118 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.118 | Temperature_cooling_setpoint_1.118 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.118
R.1.120 | PIR_Activity_1.120 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.120 |  |  |  | ZoneAktiv | [5 empty] | 32
R.1.120 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.120/Logninger
R.1.120 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.120/Logninger
R.1.120 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.120/Logninger
R.1.120 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Heating_valve_1.120 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Temperature_heating_setpoint_1.120 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Temperature_cooling_setpoint_1.120 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Damper_position_supply | Position of the supply damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.120 | Valve_cooling | Valve for cooling in the ventilation | /TM023_2_20_1.103B/Lon/Net/Rum 1.120
R.1.126 | PIR_Activity_1.126 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.126 |  |  |  | ZoneAktiv | [5 empty] | 33
R.1.126 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.126/Logninger
R.1.126 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.126/Logninger
R.1.126 | 00_Luftmængde Log | Ventilation flow | /TM023_2_20_1.103B/Modbus Master Network/LabVent_1_126
R.1.126 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Heating_valve_1.126 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Temperature_heating_setpoint_1.126 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Temperature_cooling_setpoint_1.126 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | Valve_cooling | Valve for cooling in the ventilation | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.126 | CO2_setpoint | CO2 setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.126
R.1.128 | PIR_Activity_1.128 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.128 |  |  |  | ZoneAktiv | [5 empty] | 34
R.1.128 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.128/Logninger
R.1.128 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.128/Logninger
R.1.128 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.128/Logninger
R.1.128 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Heating_valve_1.128 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Temperature_heating_setpoint_1.128 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Temperature_cooling_setpoint_1.128 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.128 | Vindue_1.128 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_2_20_1.103B/Lon/Net/Rum 1.128
R.1.129 | PIR_Activity_1.129 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.129 |  |  |  | ZoneAktiv | [5 empty] | 35
R.1.129 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.129/Logninger
R.1.129 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.129/Logninger
R.1.129 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.129/Logninger
R.1.129 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Heating_valve_1.129 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Temperature_heating_setpoint_1.129 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Temperature_cooling_setpoint_1.129 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.129 | Vindue_1.129 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_2_20_1.103B/Lon/Net/Rum 1.129
R.1.130 | PIR_Activity_1.130 | If the room is considered active | /TM023_2_20_1.103B/Lon/Net/Rum 1.130 |  |  |  | ZoneAktiv | [5 empty] | 36
R.1.130 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B/Lon/Net/Rum 1.130/Logninger
R.1.130 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.130/Logninger
R.1.130 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.130/Logninger
R.1.130 | Ventilation_flow | Ventilation flow | /TM023_2_20_1.103B/Modbus Master Network/LabVent_1_130
R.1.130 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Light_ON_OFF | ON/OFF of the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Light_level_room | Light level setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | CO2_level | Current measured CO2 level in the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Temperature_global_setpoint | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Heating_valve_1.130 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Temperature_heating_setpoint_1.130 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.130 | Temperature_cooling_setpoint_1.130 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.130
R.1.132 | CO2_setpoint_1.132 | Current upper limit setpoint for the CO2 level | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | CO201_SV | [5 empty] | 45
R.1.132 | Light_off_switch_high_lux_1.132 | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | EK10 | [5 empty] | 46
R.1.132 | Lux_level_setpoint_1.132 | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | LUX01Setpunkt | [5 empty] | 47
R.1.132 | Manual_light_on_off_switch_1.132 | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | LYS_STR350_man | [5 empty] | 48
R.1.132 | Light_automatic_off_delay_1.132 | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | PIR01DelayOff | [5 empty] | 49
R.1.132 | PIR_1.132 | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | PIR01 | [5 empty] | 50
R.1.132 | Ventilation_off_delay_1.132 | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | VentForsStop | [5 empty] | 51
R.1.132 | Ventilation_AHU_status_1.132 | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | VentStatus | [5 empty] | 52
R.1.132 | Heating_valve_1.132 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | TA01 | [5 empty] | 53
R.1.132 | Temperature_offset_from_global_1.132 | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | TRU01_OffSet | [5 empty] | 54
R.1.132 | Temperature_cooling_setpoint_1.132 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | TRU01KalkKøl | [5 empty] | 55
R.1.132 | Temperature_heating_setpoint_1.132 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | TRU01KalkVarme | [5 empty] | 56
R.1.132 | Temperature_global_setpoint_1.132 | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.132 |  |  |  | TRU01SetVærdi | [5 empty] | 57
R.1.132 | Damper_position_1.132 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | VAV01_02 |  |  | 1 | 11000 | 7.6389 | 37
R.1.132 | Lux_meter_1.132 | Light level measured in the ceiling | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | LUX01 |  |  | 1 | 11000 | 7.6389 | 38
R.1.132 | Light_ON_OFF_1.132 | ON/OFF of the light | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | LY01 |  |  | 1 | 11000 | 7.6389 | 39
R.1.132 | Light_level_1.132 | Light level setpoint | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | LN01 |  |  | 1 | 11000 | 7.6389 | 40
R.1.132 | PIR_Activity_1.132 | If the room is considered active | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | ZoneAktiv |  |  | 1 | 11000 | 7.6389 | 41
R.1.132 | Room_temperature_1.132 | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | TRU01 |  |  | 1 | 11000 | 7.6389 | 42
R.1.132 | CO2_level_1.132 | Current measured CO2 level in the room | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | CO201 |  |  | 1 | 11000 | 7.6389 | 43
R.1.132 | Window_position_1.132 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | VINDUE_ÅBEN |  |  | 1 | 11000 | 7.6389 | 44
R.1.132 | Vindue_1.132 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_2_20_1.103B/Lon/Net/Rum 1.132
R.1.132 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.132
R.1.132 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.132
R.1.132 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.132
R.1.136 | CO2_setpoint_1.136 | Current upper limit setpoint for the CO2 level | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | CO201_SV | [5 empty] | 8
R.1.136 | Light_off_switch_high_lux_1.136 | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | EK10 | [5 empty] | 9
R.1.136 | Lux_level_setpoint_1.136 | Light level setpoint for when to switch off the light | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | LUX01Setpunkt | [5 empty] | 10
R.1.136 | Manual_light_on_off_switch_1.136 | Manual ON/OFF switch for the light located in the room control panel | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | LYS_STR350_man | [5 empty] | 11
R.1.136 | Light_automatic_off_delay_1.136 | Delay between the room being active and when the light is turned off automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | PIR01DelayOff | [5 empty] | 12
R.1.136 | Lux_level_ceiling_1.136 | Light level measured in the ceiling | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | LUX01 | [5 empty] | 13
R.1.136 | Ventilation_off_delay_1.136 | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | VentForsStop | [5 empty] | 14
R.1.136 | Ventilation_AHU_status_1.136 | Status of the AHU supplying the room | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | VentStatus | [5 empty] | 15
R.1.136 | Heating_valve_1.136 | Opening signal of the radiator valve | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | TA01 | [5 empty] | 16
R.1.136 | Temperature_offset_from_global_1.136 | Offset from the global temperature setpoint (manually set by the user) | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | TRU01_OffSet | [5 empty] | 17
R.1.136 | Temperature_cooling_setpoint_1.136 | Upper limit for activating cooling | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | TRU01KalkKøl | [5 empty] | 18
R.1.136 | Temperature_heating_setpoint_1.136 | Lower limit for activating heating | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | TRU01KalkVarme | [5 empty] | 19
R.1.136 | Temperature_global_setpoint_1.136 | Global temperature setpoint | /TM023_2_20_1.103B/Lon/Net/Rum 1.136 |  |  |  | TRU01SetVærdi | [5 empty] | 20
R.1.136 | Damper_position_1.136 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | VAV01_02 |  |  | 1 | 11000 | 7.6389 | 58
R.1.136 | Lux_meter_1.136 | Measurement from the PIR sensor to determine if occupied or not | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | PIR01 |  |  | 1 | 11000 | 7.6389 | 59
R.1.136 | Light_ON_OFF_1.136 | ON/OFF of the light | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | LY01 |  |  | 1 | 11000 | 7.6389 | 0
R.1.136 | Light_level_1.136 | Light level setpoint | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | LN01 |  |  | 1 | 11000 | 7.6389 | 1
R.1.136 | PIR_activity_1.136 | If the room is considered active | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | ZoneAktiv |  |  | 1 | 11000 | 7.6389 | 4
R.1.136 | Room_temperature_1.136 | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | TRU01 |  |  | 1 | 11000 | 7.6389 | 5
R.1.136 | CO2_1.136 | Current measured CO2 level in the room | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | CO201 |  |  | 1 | 11000 | 7.6389 | 6
R.1.136 | window_position_1.136 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_2_20_1.103B |  | CHART_FLOOR_LEVEL_1 | /TM023_2_20_1.103B | VINDUE_ÅBEN |  |  | 1 | 11000 | 7.6389 | 7
R.1.136 | Light_blackboard | Light at the blackboard | /TM023_2_20_1.103B/Lon/Net/Rum 1.136
R.1.136 | Room_temp_deadband_day | Deadband during daytime | /TM023_2_20_1.103B/Lon/Net/Rum 1.136
R.1.136 | Room_temp_deadband_standby | Deadband during standby | /TM023_2_20_1.103B/Lon/Net/Rum 1.136
R.1.136 | Room_temp_deadband_night | Deadband during nighttime | /TM023_2_20_1.103B/Lon/Net/Rum 1.136
R.1.201 | PIR_activity_1.201 | If the room is considered active | /TM023_3_20_1.204/Lon/Net/Rum 1.201 |  |  |  | ZoneAktiv | [5 empty] | 42
R.1.201 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_3_20_1.204/Lon/Net/Rum 1.201/Logninger
R.1.201 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_3_20_1.204/Lon/Net/Rum 1.201/Logninger
R.1.201 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_3_20_1.204/Lon/Net/Rum 1.201/Logninger
R.1.201 | Temperature_heating_setpoint_1.201 | Lower limit for activating heating | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Temperature_cooling_setpoint_1.201 | Upper limit for activating cooling | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Light_ON_OFF | ON/OFF of the light | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Light_level_room | Light level setpoint | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | CO2_level | Current measured CO2 level in the room | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Vindue_1.201 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_3_20_1.204/Lon/Net/Rum 1.201/Logninger
R.1.201 | Temperature_global_setpoint | Global temperature setpoint | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Room_temp_deadband_day | Deadband during daytime | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Room_temp_deadband_standby | Deadband during standby | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Room_temp_deadband_night | Deadband during nighttime | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Ventilation_off_delay | Delay between the room being active and when the ventilation dampers are closed automatically | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Lux_level_setpoint | Light level setpoint for when to switch off the light | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Light_automatic_off_delay | Delay between the room being active and when the light is turned off automatically | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.201 | Heating_valve_1.201 | Opening signal of the radiator valve | /TM023_3_20_1.204/Lon/Net/Rum 1.201
R.1.203 | PIR_activity_1.203 | If the room is considered active | /TM023_3_20_1.204/Lon/Net/Rum 1.203 |  |  |  | ZoneAktiv | [5 empty] | 43
R.1.203 | VAV01 | Position of the supply/extraction damper in VAV supplied rooms | /TM023_3_20_1.204/Lon/Net/Rum 1.203/Logninger
R.1.203 | TRU01_Rum Temp | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_3_20_1.204/Lon/Net/Rum 1.203/Logninger
R.1.203 | CO201_Rum ppm | Current measured CO2 level in the room | /TM023_3_20_1.204/Lon/Net/Rum 1.203/Logninger
R.1.203 | Temperature_heating_setpoint_1.203 | Lower limit for activating heating | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Temperature_cooling_setpoint_1.203 | Upper limit for activating cooling | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Damper_position | Position of the supply/extraction damper in VAV supplied rooms | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Lux_meter | Measurement from the PIR sensor to determine if occupied or not | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Lux_level_ceiling | Light level measured in the ceiling | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Light_ON_OFF | ON/OFF of the light | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Light_level_room | Light level setpoint | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Light_off_switch | ON/OFF switch due to high lux level in the room measured in the ceiling | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Light_roompanel | Manual ON/OFF switch for the light located in the room control panel | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Room_temperature | Measured room temperature (cannot be assumed to be either air or operative temperature) | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | R.1.203 CO2 ppm | Current measured CO2 level in the room | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Temperature_offset_from_global | Offset from the global temperature setpoint (manually set by the user) | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Ventilation_AHU_status | Status of the AHU supplying the room | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Vindue_1.203 | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | /TM023_3_20_1.204/Lon/Net/Rum 1.203/Logninger
R.1.203 | Temperature_global_setpoint | Global temperature setpoint | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Room_temp_deadband_day | Deadband during daytime | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Room_temp_deadband_standby | Deadband during standby | /TM023_3_20_1.204/Lon/Net/Rum 1.203
R.1.203 | Room_temp_deadband_night | Deadband during nighttime | /TM023_3_20_1.204/Lon/Net/Rum 1.203

## Main energy supplies
Name | Name in JSON file for the SATO platform | Name in BMS system | Variable description | Variable category | Unit
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_energy | nvoE1_HeatV1_Raw | District heating accumulated energy supplied for the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_volume | nvoV1_Volume_Raw | District heating accumulated volume supplied for the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_power | nvoPowerV1 | District heating power currently supplied to the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_flow | nvoV1_Flow | District heating flow currently supplied to the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_supply_temperature | nvoTemperature1 | District heating supply temperature currently supplied to the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_return_temperature | nvoTemperature2 | District heating return temperature currently supplied from the whole building | District heating
FO01_QMV01 | /TM023_0_20_1128/Lon/Net/FO01_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DH_whole_building_operation_hours | nvoHourCount | District heating accumulated number of operation hours for the whole building | District heating
HT00-1_EM01 | /TM023_0_20_1121/Modbus Com B/HT.00-1-EM01/PM710/Modbus Signals/EL_whole_building_power | Real Power, Total | Electrical power supplied to the whole building | Electrical
HT00-1_EM01 | /TM023_0_20_1121/Modbus Com B/HT.00-1-EM01/PM710/Modbus Signals/EL_whole_building_energy | Signed Real Energy, Consumption | Accumulated electrical energy supplied to the whole building | Electrical
BK01_KVM01 | /TM023_0_20_1128/Lon/Net/BK01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DCW_whole_building_volume | nvoV1_Volume_Raw | Domestic cold water accumulated volume supplied to the whole building | Domestic cold water
BK01_KVM01 | /TM023_0_20_1128/Lon/Net/BK01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DCW_whole_building_flow | nvoV1_Flow | Domestic cold water current flow supplied to the whole building | Domestic cold water
BK01_KVM01 | /TM023_0_20_1128/Lon/Net/BK01_KVM01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/DCW_whole_building_operation_hours | nvoHourCount | Domestic cold water accumulated number of operation hours for the whole building | Domestic cold water

## AHUs
Name | Name in JSON file for the SATO platform | Name in BMS system | Variable description | Variable category | Unit | Name in BMS system |  | Variable description | Variable category | Number in picture
KOMF01 | /TM023_0_23_1.125/ATV_control | ATV control/FE29 | Exhaust fan power | Fan | kW | KOMF01 | KOMF02 | - | - | -
KOMF01 | /TM023_0_23_1.125/KOMF01/Air_flow_KOMF01 | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h | Exhaust fan flow | Fan | m^3/h | ATV control/FE29 | ATV control/FE29 | Exhaust fan power | Fan | 1
KOMF01 | /TM023_0_23_1.125/KOMF01/Pressure_diff_fan | SXW_VEN_Rotorveksler_000K/PDU01 | Exhaust fan pressure difference | Fan | Pa | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h | Exhaust fan flow | Fan | 2
KOMF01 | /TM023_0_23_1.125/KOMF01/Exhaust_fan_start | VU01_K | Exhaust fan on/off signal | Fan | Boolean | SXW_VEN_Rotorveksler_000K/PDU01 | SXW_VEN_Rotorveksler_000K/PDU01 | Exhaust fan pressure difference | Fan | 3
KOMF01 | /TM023_0_23_1.125/KOMF01/Alarm_filter_exhaust | PFU01_F | Extraction filter pressure | Alarm | Boolean | VU01_K | VU01_K | Exhaust fan on/off signal | Fan | 4
KOMF01 | /TM023_0_23_1.125/KOMF01/Alarm_intake_filter | PFU01_F | Intake filter pressure | Alarm | Boolean | PFU01_F | PFU01_F | Extraction filter pressure | Alarm | 5
KOMF01 | /TM023_0_23_1.125/KOMF01/ATV_control_supply | ATV control/FE29 | Supply fan power | Fan | kW | PFU01_F | PFI01_F | Intake filter pressure | Alarm | 6
KOMF01 | /TM023_0_23_1.125/KOMF01/Air_flow_supply | VI01_FLOW_m3_h | Supply fan flow | Fan | m^3/h | ATV control/FE29 | ATV control/FE29 | Supply fan power | Fan | 7
KOMF01 | /TM023_0_23_1.125/KOMF01/Air pressure_diff_supply | PDI01 | Supply fan pressure difference | Fan | Pa | VI01_FLOW_m3_h | VI01_FLOW_m3_h | Supply fan flow | Fan | 8
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_fan_start | VI01_K | Supply fan on/off signal | Fan | Boolean | PDI01 | PDI01 | Supply fan pressure difference | Fan | 9
KOMF01 | /TM023_0_23_1.125/KOMF01/Cooling_recovery_active_if | KØLIG_DIFF_T_AKT_SV (settings) | Activation criteria for cooling recovery: external air temperature minus extraction air temperature above threshold | Settings | °C | VI01_K | VI01_K | Supply fan on/off signal | Fan | 10
KOMF01 | /TM023_0_23_1.125/KOMF01/Cooling_recovery_inactive_if | KØLIG_DIFF_T_DEAKT_SV (settings) | Deactivation criteria for cooling recovery: extration air temperature minus external air temperature above threshold | Settings | °C | KØLIG_DIFF_T_AKT_SV (settings) | KØLG_DIFF_T_AKT_SV | Activation criteria for cooling recovery: external air temperature minus extraction air temperature above threshold | Settings | 11
KOMF01 | /TM023_0_23_1.125/KOMF01/Exhaust_fan_signal | VU01_S | Exhaust fan control signal | Fan | % | KØLIG_DIFF_T_DEAKT_SV (settings) | KØLG_DIFF_T_DEAKT_SV | Deactivation criteria for cooling recovery: extration air temperature minus external air temperature above threshold | Settings | 12
KOMF01 | /TM023_0_23_1.125/KOMF01/Exhaust_temperature | TU02 | Exhaust air temperature | Air temperature sensor | °C | VU01_S | VU01_S | Exhaust fan control signal | Fan | 13
KOMF01 | /TM023_0_23_1.125/KOMF01/Extraction_damper_on-off | SMU01_K | Extraction damper on/off signal | Damper | Boolean | TU02 | TU02 | Exhaust air temperature | Air temperature sensor | 14
KOMF01 | /TM023_0_23_1.125/KOMF01/Extraction_pressure | PTU01 | Extraction air pressure | Air pressure sensor | Pa | SMU01_K | SMU01_K | Extraction damper on/off signal | Damper | 15
KOMF01 | /TM023_0_23_1.125/KOMF01/Extraction_pressure_set-point | PTU01_SV (settings) | Extraction air pressure setpoint | Setpoint | Pa | PTU01 | PTU01 | Extraction air pressure | Air pressure sensor | 16
KOMF01 | /TM023_0_23_1.125/KOMF01/Extraction_temperature | TU01 | Extraction air temperature | Air temperature sensor | °C | PTU01_SV (settings) | PTU01_SV | Extraction air pressure setpoint | Setpoint | 17
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_control_valve | MVV01_S | Heating coil motorvalve position | Heating coil | % | TU01 | TU01 | Extraction air temperature | Air temperature sensor | 18
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_effect | power_f (energymeter) | Heating coil district heating current power output | Heating coil | W | MVV01_S | MVV01_S | Heating coil motorvalve position | Heating coil | 19
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_energy_accumulated | elec_whr_f (energymeter) | Heating coil district heating accumulated energy use | Heating coil | Wh | power_f (energymeter) | nvoPowerV1 | Heating coil district heating current power output | Heating coil | 20
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_flow | flow_f (energymeter) | Heating coil district heating current flow | Heating coil | l/s | elec_whr_f (energymeter) | nvoE1_HeatV1 | Heating coil district heating accumulated energy use | Heating coil | 21
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_operation_hours_accumulated | count_f (energymeter) | Heating coil time in operation | Heating coil | h | flow_f (energymeter) | nvoV1_Flow | Heating coil district heating current flow | Heating coil | 22
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_pump_on-off | PV01_K | Heating coil pump on/off signal | Heating coil | Boolean | count_f (energymeter) | nvoHourCount | Heating coil time in operation | Heating coil | 23
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_return_temperature | TR01 | Heating coil return water temperature | Heating coil | °C | PV01_K | PV01_K | Heating coil pump on/off signal | Heating coil | 24
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_return_temperature_DH | temp_p (energymeter) | Heating coil district heating return water temperature | Heating coil | °C | TR01 | TR01 | Heating coil return water temperature | Heating coil | 25
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_return_temperature_min_limit | TR01_SV (settings) | Heating coil lowest return water temperature allowed | Heating coil | °C | temp_p (energymeter) | nvoTemperature2 | Heating coil district heating return water temperature | Heating coil | 26
KOMF01 | /TM023_0_23_1.125/KOMF01/HC_supply_temperature | TF01 | Heating coil supply water temperature | Heating coil | °C | TR01_SV (settings) | TR01_SV | Heating coil lowest return water temperature allowed | Heating coil | 27
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_supply_temperature_DH | temp_p (energymeter) | Heating coil district heating supply water temperature | Heating coil | °C | TF01 | TF01 | Heating coil supply water temperature | Heating coil | 28
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/HC_volume_accumulated | vol_f (energymeter) | Heating coil district heating accumulated volume flow | Heating coil | l | temp_p (energymeter) | nvoTemperature1 | Heating coil district heating supply water temperature | Heating coil | 29
KOMF01 | /TM023_0_23_1.125/KOMF01/HE_efficiency | VIRKNINGSGRAD | Heat recovery efficiency | Rotary heat exchanger | % | vol_f (energymeter) | nvoV1_Volume | Heating coil district heating accumulated volume flow | Heating coil | 30
KOMF01 | /TM023_0_23_1.125/KOMF01/HE_signal | RV01_S | Rotation speed | Rotary heat exchanger | % | VIRKNINGSGRAD | VIRKNINGSGRAD | Heat recovery efficiency | Rotary heat exchanger | 31
KOMF01 | /TM023_0_23_1.125/KOMF01/Intake_damper_on-off | SMI01_K | Intake damper on/off signal | Damper | Boolean | RV01_S | RV01_S | Rotation speed | Rotary heat exchanger | 32
KOMF01 | /TM023_0_23_1.125/KOMF01/Intake_temperature | TI03 | Intake air temperature | Air temperature sensor | °C | SMI01_K | SMI01_K | Intake damper on/off signal | Damper | 33
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_cooling_active_if_diff_external_temperature_and_room_temperature_above | NATKØL_SV_D_TUD_TRU (settings) | Activation criteria for night cooling: room temperature minus external air temperature above threshold | Settings | °C | TI03 | TI03 | Intake air temperature | Air temperature sensor | 34
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_cooling_active_if_external_temperature_above | NATKØL_SV_LAV_TUD01 (settings) | Activation criteria for night cooling: external air temperature above threshold | Settings | °C | NATKØL_SV_D_TUD_TRU (settings) | NATKØL_SV_D_TUD_TRU | Activation criteria for night cooling: room temperature minus external air temperature above threshold | Settings | 35
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_cooling_active_if_room_temperature_above | NATKØL_SV_TRU01 (settings) | Activation criteria for night cooling: room temperature above threshold | Settings | °C | NATKØL_SV_LAV_TUD01 (settings) | NATKØL_SV_LAV_TUD01 | Activation criteria for night cooling: external air temperature above threshold | Settings | 36
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_cooling_max_operation_hours_per_day | NATKØL_SV_TIM_START (settings) | Maximum hours night cooling can be activated in one night | Settings | h | NATKØL_SV_TRU01 (settings) | NATKØL_SV_TRU01 | Activation criteria for night cooling: room temperature above threshold | Settings | 37
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_heating_active_if_room_temperature_below | NATVARME_SV_TRU01 (settings) | Activation cireteria for night heating: room temperature below threshold | Settings | °C | NATKØL_SV_TIM_START (settings) | NATKØL_SV_TIM_START | Maximum hours night cooling can be activated in one night | Settings | 38
KOMF01 | /TM023_0_23_1.125/KOMF01/Night_heating_max_operation_hours_per_day | NATVAR_SV_TIM_START (settings) | Maximum hours night heating can be activated in one night | Settings | h | NATVARME_SV_TRU01 (settings) | NATVARME_SV_TRU01 | Activation cireteria for night heating: room temperature below threshold | Settings | 39
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_fan_signal | VI01_S | Supply fan control signal | Fan | % | NATVAR_SV_TIM_START (settings) | NATVAR_SV_TIM_START | Maximum hours night heating can be activated in one night | Settings | 40
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_pressure | PTI01 | Supply air pressure | Air pressure sensor | Pa | VI01_S | VI01_S | Supply fan control signal | Fan | 41
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_pressure_set-point | PTI01_SV (settings) | Supply air pressure setpoint | Setpoint | Pa | PTI01 | PTI01 | Supply air pressure | Air pressure sensor | 42
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature | TI01 | Supply air temperature | Air temperature sensor | °C | PTI01_SV (settings) | PTI01_SV | Supply air pressure setpoint | Setpoint | 43
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X | TI01_KURVE_X (settings) | External air temperature (should be the same for both AHUs) | Air temperature sensor | °C | TI01 | TI01 | Supply air temperature | Air temperature sensor | 44
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X1 | TI01_KURVE_X1 (settings) | - | Settings | °C | TI01_KURVE_X (settings) | - | External air temperature (should be the same for both AHUs) | Air temperature sensor | 45
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X2 | TI01_KURVE_X2 (settings) | - | Settings | °C | TI01_KURVE_X1 (settings) | - | - | Settings | 46
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X3 | TI01_KURVE_X3 (settings) | - | Settings | °C | TI01_KURVE_X2 (settings) | - | - | Settings | 47
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_Y | TI01_KURVE (settings) | - | Settings | °C | TI01_KURVE_X3 (settings) | - | - | Settings | 48
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_Y1 | TI01_KURVE_Y1 (settings) | - | Settings | °C | TI01_KURVE (settings) | - | - | Settings | 49
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_Y2 | TI01_KURVE_Y2 (settings) | - | Settings | °C | TI01_KURVE_Y1 (settings) | - | - | Settings | 50
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_Y3 | TI01_KURVE_Y3 (settings) | - | Settings | °C | TI01_KURVE_Y2 (settings) | - | - | Settings | 51
KOMF01 | /TM023_0_23_1.125/KOMF01/Supply_temperature_set-point | TI01_KALK_SV | Supply air temperature setpoint | Setpoint | °C | TI01_KURVE_Y3 (settings) | - | - | Settings | 52
KOMF01 | /TM023_0_23_1.125/KOMF01/Temperature_after_HE_before_HC | TI02 | Air temperature after HE | Air temperature sensor | °C | TI01_KALK_SV | TI01_KALK_SV | Supply air temperature setpoint | Setpoint | 53
KOMF01 | /TM023_0_23_1.125/KOMF01/Winter_mode_active_if_external_temperature_below | TI01_REG_SV_LAV_UT (settings) | Activation criteria for winter mode: external air temperature below threshold | Settings | °C | TI02 | TI02 | Air temperature after HE | Air temperature sensor | 54
KOMF01 | /TM023_0_23_1.125/KOMF01/ventilation_system_status | VEN_STATUS | AHU status | Overall | Status code | TI01_REG_SV_LAV_UT (settings) | TI01_REG__SV_LAV_UT | Activation criteria for winter mode: external air temperature below threshold | Settings | 55
KOMF01 | /TM023_0_23_1.125/IO Bus/M3_UI-16/Heat_coil_alarm | TFI01 | Heating coil temperature | Alarm | Boolean | VEN_STATUS | VEN_STATUS | AHU status | Overall | 56
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_Extended_run_time_ventilation_system | DT01_FORL_DR_TID_SV | Manual override for extending the running time of the ahu | Settings | min | TFI01 | TFI01 | Heating coil temperature | Alarm | 57
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_status_extended_run_time | DT01_FORL_DRIFT | Status of the manual override for extending the running time of the AHU | Settings | Boolean | DT01_FORL_DR_TID_SV | DT01_FORL_DR_TID_SV | Manual override for extending the running time of the ahu | Settings | 58
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_supply_temperature | TI01_SV | - | Settings | °C | DT01_FORL_DRIFT | DT01_FORL_DRIFT | Status of the manual override for extending the running time of the AHU | Settings | 59
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_desired_room_temperature | TRU01_SV | - | Settings | °C | TI01_SV | TI01_SV | - | Settings | 60
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_max_inlet_temp | TI01_KALK_TRU_MAX_SV | - | Settings | °C | TRU01_SV | TRU01_SV | - | Settings | 61
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_min_inlet_temp | TI01_KALK_TRU_MIN_SV | - | Settings | °C | TI01_KALK_TRU_MAX_SV | TI01_KALK_TRU_MAX_SV | - | Settings | 62
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_desired_outlet_temp | TU01_SV | - | Settings | °C | TI01_KALK_TRU_MIN_SV | TI01_KALK_TRU_MIN_SV | - | Settings | 63
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_max_outlet_temp | TI01_KALK_TU_MAX_SV | - | Settings | °C | TU01_SV | TU01_SV | - | Settings | 64
KOMF01 | /TM023_0_23_1.125/KOMF01/Setting_min_outlet_temp | TI01_KALK_TU_MIN_SV | - | Settings | °C | TI01_KALK_TU_MAX_SV | TI01_KALK_TU_MAX_SV | - | Settings | 65
KOMF01 | /TM023_0_23_1.125/KOMF01/Temperature_room_1.136 | 1136_TRU01 | Reference room temperature | Overall | °C | TI01_KALK_TU_MIN_SV | TI01_KALK_TU_MIN_SV | - | Settings | 66
KOMF01 | /TM023_0_23_1.125/KOMF01/Temperature_room_1.255 | 1255_TRU01 | Reference room temperature | Overall | °C | 1136_TRU01 | 1104_TRU01 | Reference room temperature | Overall | 67
KOMF01 | /TM023_0_23_1.125/KOMF01/Temperature_room_1.365 | 1365_TRU01 | Reference room temperature | Overall | °C | 1255_TRU01 | 1218_TRU01 | Reference room temperature | Overall | 68
KOMF01 | /TM023_0_23_1.125/KOMF01/SEL_value | SEL_VÆRDI_J_m3 | SEL value | Fan | J/m^3 | 1365_TRU01 | 1316_TRU01 | Reference room temperature | Overall | 69
KOMF01 | /TM023_0_23_1.125/Lon/Net/KOMF01-EM01/EnergyMeter/EnergyMeas [1]/nvoPartialkWh Log | elec_kwh_l | Total electricity use of AHU | Overall | kWh | SEL_VÆRDI_J_m3 | SEL_VÆRDI_J_m3 | SEL value | Fan | 70
KOMF02 | /TM023_0_20_1.011/ModbusA VEXX/ATV212 KOMF02 VU01/ATV_power_exhaust | ATV control/FE29 | Exhaust fan power | Fan | kW | elec_kwh_l | elec_kwh_l | Total electricity use of AHU | Overall | 71
KOMF02 | /TM023_0_20_1.011/KOMF02/Exhaust_flow | SXW_VEN_Rotorveksler_000K/VU01_FLOW_m3_h | Exhaust fan flow | Fan | m^3/h
KOMF02 | /TM023_0_20_1.011/KOMF02/Pressure_diff_fan | SXW_VEN_Rotorveksler_000K/PDU01 | Exhaust fan pressure difference | Fan | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Fan_exhaust_status | VU01_K | Exhaust fan on/off signal | Fan | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Alarm_filter_exhaust | PFU01_F | Extraction filter pressure | Alarm | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Alarm_filter_intake | PFI01_F | Intake filter pressure | Alarm | Boolean
KOMF02 | /TM023_0_20_1.011/ModbusA VEXX/ATV212 KOMF02 VI01/ATV_power_supply | ATV control/FE29 | Supply fan power | Fan | kW
KOMF02 | /TM023_0_20_1.011/KOMF02/Air_flow_supply | VI01_FLOW_m3_h | Supply fan flow | Fan | m^3/h
KOMF02 | /TM023_0_20_1.011/KOMF02/Pressure_diff_fan_supply | PDI01 | Supply fan pressure difference | Fan | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Fan_intake_status | VI01_K | Supply fan on/off signal | Fan | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_cooling_recovery_active_setpoint | KØLG_DIFF_T_AKT_SV | Activation criteria for cooling recovery: external air temperature minus extraction air temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_cooling_recovery_inactive_setpoint | KØLG_DIFF_T_DEAKT_SV | Deactivation criteria for cooling recovery: extration air temperature minus external air temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Fan_exhaust_speed | VU01_S | Exhaust fan control signal | Fan | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_exhaust_after_heatexchange | TU02 | Exhaust air temperature | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Damper_exhaust | SMU01_K | Extraction damper on/off signal | Damper | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Exhaust_pressure | PTU01 | Extraction air pressure | Air pressure sensor | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_outlet_pressure | PTU01_SV | Extraction air pressure setpoint | Setpoint | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_exhaust | TU01 | Extraction air temperature | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Motor_valve_heat_coil | MVV01_S | Heating coil motorvalve position | Heating coil | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Energy_heat_coil | nvoPowerV1 | Heating coil district heating current power output | Heating coil | W
KOMF02 | /TM023_0_20_1.011/KOMF02/Total_energy_heat_coil | nvoE1_HeatV1 | Heating coil district heating accumulated energy use | Heating coil | Wh
KOMF02 | /TM023_0_20_1.011/KOMF02/Flow_heat_coil | nvoV1_Flow | Heating coil district heating current flow | Heating coil | l/s
KOMF02 | /TM023_0_20_1.011/KOMF02/Hour_counter_heating_coil | nvoHourCount | Heating coil time in operation | Heating coil | h
KOMF02 | /TM023_0_20_1.011/KOMF02/Heat_coil_pump | PV01_K | Heating coil pump on/off signal | Heating coil | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_return_heat_coil | TR01 | Heating coil return water temperature | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Return_temp_heat_coil | nvoTemperature2 | Heating coil district heating return water temperature | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_min_return_temp_heating_coil | TR01_SV | Heating coil lowest return water temperature allowed | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_supply_heat_coil | TF01 | Heating coil supply water temperature | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Supply_temp_heat_coil | nvoTemperature1 | Heating coil district heating supply water temperature | Heating coil | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Total_volume_heat_coil | nvoV1_Volume | Heating coil district heating accumulated volume flow | Heating coil | l
KOMF02 | /TM023_0_20_1.011/KOMF02/Heat_exchanger_efficiency | VIRKNINGSGRAD | Heat recovery efficiency | Rotary heat exchanger | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Heat_exchanger_speed | RV01_S | Rotation speed | Rotary heat exchanger | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Damper_intake | SMI01_K | Intake damper on/off signal | Damper | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_intake | TI03 | Intake air temperature | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_night_cooling_when_outdoor_temp_below_room_temp | NATKØL_SV_D_TUD_TRU | Activation criteria for night cooling: room temperature minus external air temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_night_cooling_room_temp_outdoor_temp | NATKØL_SV_LAV_TUD01 | Activation criteria for night cooling: external air temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_night_cooling_room_temp | NATKØL_SV_TRU01 | Activation criteria for night cooling: room temperature above threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_max_time_night_cooling | NATKØL_SV_TIM_START | Maximum hours night cooling can be activated in one night | Settings | h
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_night_heating | NATVARME_SV_TRU01 | Activation cireteria for night heating: room temperature below threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_max_time_night_heating | NATVAR_SV_TIM_START | Maximum hours night heating can be activated in one night | Settings | h
KOMF02 | /TM023_0_20_1.011/KOMF02/Fan_intake_speed | VI01_S | Supply fan control signal | Fan | %
KOMF02 | /TM023_0_20_1.011/KOMF02/Intake_pressure | PTI01 | Supply air pressure | Air pressure sensor | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_inlet_pressure | PTI01_SV | Supply air pressure setpoint | Setpoint | Pa
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_inlet | TI01 | Supply air temperature | Air temperature sensor | °C
KOMF02 | /TM023_0_23_1.125/KOMF01/Supply_temperature_curve_X | TI01_KURVE_X (settings) | External air temperature (should be the same for both AHUs) | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_setpoint_inlet | TI01_KALK_SV | Supply air temperature setpoint | Setpoint | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temp_before_heat_coil | TI02 | Air temperature after HE | Air temperature sensor | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_winther_start_up_temp | TI01_REG__SV_LAV_UT | Activation criteria for winter mode: external air temperature below threshold | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/ventilation_system_status | VEN_STATUS | AHU status | Overall | Status code
KOMF02 | /TM023_0_20_1.011/KOMF02/Heat_coil_alarm | TFI01 | Heating coil temperature | Alarm | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_Extended_run_time_ventilation_system | DT01_FORL_DR_TID_SV | Manual override for extending the running time of the ahu | Settings | min
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_status_extended_run_time | DT01_FORL_DRIFT | Status of the manual override for extending the running time of the AHU | Settings | Boolean
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_supply_temperature | TI01_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_desired_room_temperature | TRU01_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_max_inlet_temp | TI01_KALK_TRU_MAX_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_min_inlet_temp | TI01_KALK_TRU_MIN_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_desired_outlet_temp | TU01_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_max_outlet_temp | TI01_KALK_TU_MAX_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Setting_min_outlet_temp | TI01_KALK_TU_MIN_SV | - | Settings | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temperature_room_1.104 | 1104_TRU01 | Reference room temperature | Overall | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temperature_room_1.218 | 1218_TRU01 | Reference room temperature | Overall | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/Temperature_room_1.316 | 1316_TRU01 | Reference room temperature | Overall | °C
KOMF02 | /TM023_0_20_1.011/KOMF02/SEL_value | SEL_VÆRDI_J_m3 | SEL value | Fan | J/m^3
KOMF02 | /TM023_0_20_1.011/Lon/Net/KOMF02-EM01/EnergyMeter/EnergyMeas [1]/nvoPartialkWh Log | elec_kwh_l | Total electricity use of AHU | Overall | kWh
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45 - 52
53
54
55
56
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71

## Rooms
Name | Name in JSON file for the SATO platform | Name in BMS system | Variable description | Variable category | Unit | Variable category | Variable | Unit | Included? | Variable description | Number in picture
R.1.132 | /TM023_2_20_1.103B/Damper_position_1.132 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | % | CO2 | CO201 | ppm | X | Current measured CO2 level in the room | 1
R.1.132 | /TM023_2_20_1.103B/Lux_meter_1.132 | LUX01 | Light level measured in the ceiling | Light | Lux | CO2 | CO201_SV | ppm | X | Current upper limit setpoint for the CO2 level | 2
R.1.132 | /TM023_2_20_1.103B/Light_ON_OFF_1.132 | LY01 | ON/OFF of the light | Light | Boolean | Light | EK10 | Boolean | X | ON/OFF switch due to high lux level in the room measured in the ceiling | 3
R.1.132 | /TM023_2_20_1.103B/Light_level_1.132 | LN01 | Light level setpoint | Light | % | Light | LN01 | % | X | Light level setpoint | 4
R.1.132 | /TM023_2_20_1.103B/PIR_Activity_1.132 | ZoneAktiv | If the room is considered active | Occupancy | Boolean | Light | LN02 | % | (X) | Additional light level setpoint (only relevant for some rooms)
R.1.132 | /TM023_2_20_1.103B/Room_temperature_1.132 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C | Light | LUX01 | Lux | X | Light level measured in the ceiling | 5
R.1.132 | /TM023_2_20_1.103B/CO2_level_1.132 | CO201 | Current measured CO2 level in the room | CO2 | ppm | Light | LUX01Setpunkt | Lux | X | Light level setpoint for when to switch off the light | 6
R.1.132 | /TM023_2_20_1.103B/Window_position_1.132 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean | Light | LY01 | Boolean | X | ON/OFF of the light | 7
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/CO2_setpoint_1.132 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm | Light | LY02 | Boolean | (X) | Additional ON/OFF of the light (only relevant for some rooms)
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Light_off_switch_high_lux_1.132 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean | Light | LYS_STR350_man | Boolean | X | Manual ON/OFF switch for the light located in the room control panel | 8
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Lux_level_setpoint_1.132 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux | Occupancy | PIR01DelayOff | s | X | Delay between the room being active and when the light is turned off automatically | 9
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Manual_light_on_off_switch_1.132 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean | Occupancy | PIR01 | Boolean | X | Measurement from the PIR sensor to determine if occupied or not | 10
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Light_automatic_off_delay_1.132 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s | Occupancy | ZoneAktiv | Boolean | X | If the room is considered active | 11
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/PIR_1.132 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean | Ventilation | SMIU01 | Boolean | (X) | ON/OFF signal for the supply/extraction damper in CAV supplied rooms | 12
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Ventilation_off_delay_1.132 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s | Ventilation | VAV01_02 | % | (X) | Position of the supply/extraction damper in VAV supplied rooms | 12
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Ventilation_AHU_status_1.132 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code | Ventilation | VentForsStop | s | X | Delay between the room being active and when the ventilation dampers are closed automatically | 13
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Heating_valve_1.132 | TA01 | Opening signal of the radiator valve | Heating | % | Ventilation | VentStatus | Status code | X | Status of the AHU supplying the room | 14
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Temperature_offset_from_global_1.132 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C | Window | VINDUE_ÅBEN | Boolean | X | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | 15
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Temperature_cooling_setpoint_1.132 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C | Heating | TA01 | % | X | Opening signal of the radiator valve | 16
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Temperature_heating_setpoint_1.132 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C | Temperature | TRU01 | °C | X | Measured room temperature (cannot be assumed to be either air or operative temperature) | 17
R.1.132 | /TM023_2_20_1.103B/Lon/Net/Rum 1.132/Temperature_global_setpoint_1.132 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C | Temperature | TRU01_OffSet | °C | X | Offset from the global temperature setpoint (manually set by the user) | 18
R.1.136 | /TM023_2_20_1.103B/Damper_position_1.136 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | % | Temperature | TRU01DødZoneDag | °C | (X) | Deadband during daytime | 19
R.1.136 | /TM023_2_20_1.103B/Lux_meter_1.136 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean | Temperature | TRU01DødZoneNat | °C | (X) | Deadband during nighttime | 20
R.1.136 | /TM023_2_20_1.103B/Light_ON_OFF_1.136 | LY01 | ON/OFF of the light | Light | Boolean | Temperature | TRU01DødZoneStandby | °C | (X) | Deadband during standby | 21
R.1.136 | /TM023_2_20_1.103B/Light_level_1.136 | LN01 | Light level setpoint | Light | % | Temperature | TRU01KalkKøl | °C | X | Upper limit for activating cooling | 22
R.1.136 | /TM023_2_20_1.103B/Light_level_blackboard | LN02 | Additional light level setpoint (only relevant for some rooms) | Light | % | Temperature | TRU01KalkVarme | °C | X | Lower limit for activating heating | 23
R.1.136 | /TM023_2_20_1.103B/Light_ON_OFF_blackboard | LY02 | Additional ON/OFF of the light (only relevant for some rooms) | Light | Boolean | Temperature | TRU01SetVærdi | °C | X | Global temperature setpoint | 24
R.1.136 | /TM023_2_20_1.103B/PIR_activity_1.136 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.136 | /TM023_2_20_1.103B/Room_temperature_1.136 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.136 | /TM023_2_20_1.103B/CO2_1.136 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.136 | /TM023_2_20_1.103B/window_position_1.136 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/CO2_setpoint_1.136 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Light_off_switch_high_lux_1.136 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Lux_level_setpoint_1.136 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Manual_light_on_off_switch_1.136 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Light_automatic_off_delay_1.136 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Lux_level_ceiling_1.136 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Ventilation_off_delay_1.136 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Ventilation_AHU_status_1.136 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Heating_valve_1.136 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Temperature_offset_from_global_1.136 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Temperature_cooling_setpoint_1.136 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Temperature_heating_setpoint_1.136 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.136 | /TM023_2_20_1.103B/Lon/Net/Rum 1.136/Temperature_global_setpoint_1.136 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.248 | /TM023_3_21_1.204/Damper_position_1.248 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.248 | /TM023_3_21_1.204/Lux_meter_1.248 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.248 | /TM023_3_21_1.204/Light_ON_OFF_1.248 | LY01 | ON/OFF of the light | Light | Boolean
R.1.248 | /TM023_3_21_1.204/Light_level_1.248 | LN01 | Light level setpoint | Light | %
R.1.248 | /TM023_3_21_1.204/PIR_activity_1.248 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.248 | /TM023_3_21_1.204/Room_temperature_1.248 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.248 | /TM023_3_21_1.204/CO2_level_1.248 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.248 | /TM023_3_21_1.204/Window_position_1.248 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/CO2_setpoint_1.248 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Light_off_switch_high_lux_1.248 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Lux_level_ceiling_1.248 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Lux_level_setpoint_1.248 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Manual_light_on_off_switch_1.248 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Light_automatic_off_delay_1.248 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Ventilation_off_delay_1.248 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.248 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Heating_valve_1.248 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Temperature_offset_from_global_1.248 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Temperature_cooling_setpoint_1.248 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Temperature_heating_setpoint_1.248 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.248 | /TM023_3_21_1.204/Lon/Net/Rum 1.248/Temperature_global_setpoint_1.248 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.250 | /TM023_3_21_1.204/Damper_position_1.250 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.250 | /TM023_3_21_1.204/Lux_meter_1.250 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.250 | /TM023_3_21_1.204/Light_ON_OFF_1.250 | LY01 | ON/OFF of the light | Light | Boolean
R.1.250 | /TM023_3_21_1.204/Light_level_1.250 | LN01 | Light level setpoint | Light | %
R.1.250 | /TM023_3_21_1.204/PIR_activity_1.250 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.250 | /TM023_3_21_1.204/Room_temperature_1.250 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.250 | /TM023_3_21_1.204/CO2_level_1.250 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.250 | /TM023_3_21_1.204/Window_position_1.250 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/CO2_setpoint_1.250 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Light_off_switch_high_lux_1.250 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Lux_level_ceiling_1.250 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Lux_level_setpoint_1.250 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Manual_light_on_off_switch_1.250 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Light_automatic_off_delay_1.250 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Ventilation_off_delay_1.250 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.250 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Heating_valve_1.250 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Temperature_offset_from_global_1.250 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Temperature_cooling_setpoint_1.250 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Temperature_heating_setpoint_1.250 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.250 | /TM023_3_21_1.204/Lon/Net/Rum 1.250/Temperature_global_setpoint_1.250 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.252 | /TM023_3_21_1.204/Damper_position_1.252 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.252 | /TM023_3_21_1.204/Lux_meter_1.252 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.252 | /TM023_3_21_1.204/Light_ON_OFF_1.252 | LY01 | ON/OFF of the light | Light | Boolean
R.1.252 | /TM023_3_21_1.204/Light_level_1.252 | LN01 | Light level setpoint | Light | %
R.1.252 | /TM023_3_21_1.204/PIR_activity_1.252 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.252 | /TM023_3_21_1.204/Room_temperature_1.252 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.252 | /TM023_3_21_1.204/CO2_level_1.252 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.252 | /TM023_3_21_1.204/Window_position_1.252 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/CO2_setpoint_1.252 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Light_off_switch_high_lux_1.252 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Lux_level_ceiling_1.252 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Lux_level_setpoint_1.252 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Manual_light_on_off_switch_1.252 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Light_automatic_off_delay_1.252 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Ventilation_off_delay_1.252 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.252 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Heating_valve_1.252 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Temperature_offset_from_global_1.252 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Temperature_cooling_setpoint_1.252 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Temperature_heating_setpoint_1.252 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.252 | /TM023_3_21_1.204/Lon/Net/Rum 1.252/Temperature_global_setpoint_1.252 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.253 | /TM023_3_21_1.204/Damper_position_1.253 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.253 | /TM023_3_21_1.204/Lux_meter_1.253 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.253 | /TM023_3_21_1.204/Light_ON_OFF_1.253 | LY01 | ON/OFF of the light | Light | Boolean
R.1.253 | /TM023_3_21_1.204/Light_level_1.253 | LN01 | Light level setpoint | Light | %
R.1.253 | /TM023_3_21_1.204/PIR_activity_1.253 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.253 | /TM023_3_21_1.204/Room_temperature_1.253 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.253 | /TM023_3_21_1.204/CO2_level_1.253 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.253 | /TM023_3_21_1.204/Window_position_1.253 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/CO2_setpoint_1.253 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Light_off_switch_high_lux_1.253 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Lux_level_setpoint_1.253 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Manual_light_on_off_switch_1.253 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Light_automatic_off_delay_1.253 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/PIR_1.253 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Ventilation_off_delay_1.253 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.253 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Heating_valve_1.253 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Temperature_offset_from_global_1.253 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Temperature_cooling_setpoint_1.253 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Temperature_heating_setpoint_1.253 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.253 | /TM023_3_21_1.204/Lon/Net/Rum 1.253/Temperature_global_setpoint_1.253 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.255 | /TM023_3_21_1.204/Damper_position_1.255 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.255 | /TM023_3_21_1.204/Lux_meter_1.255 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.255 | /TM023_3_21_1.204/Light_ON_OFF_1.255 | LY01 | ON/OFF of the light | Light | Boolean
R.1.255 | /TM023_3_21_1.204/Light_level_1.255 | LN01 | Light level setpoint | Light | %
R.1.255 | /TM023_3_21_1.204/PIR_activity_1.255 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.255 | /TM023_3_21_1.204/Room_temperature_1.255 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.255 | /TM023_3_21_1.204/CO2_level_1.255 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.255 | /TM023_3_21_1.204/Window_position_1.255 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/CO2_setpoint_1.255 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Light_off_switch_high_lux_1.255 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Lux_level_ceiling_1.255 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Lux_level_setpoint_1.255 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Manual_light_on_off_switch_1.255 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Light_automatic_off_delay_1.255 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Ventilation_off_delay_1.255 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.255 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Heating_valve_1.255 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Temperature_offset_from_global_1.255 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Temperature_cooling_setpoint_1.255 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Temperature_heating_setpoint_1.255 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.255 | /TM023_3_21_1.204/Lon/Net/Rum 1.255/Temperature_global_setpoint_1.255 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.256 | /TM023_3_21_1.204/Damper_position_1.256 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.256 | /TM023_3_21_1.204/Lux_meter_1.256 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.256 | /TM023_3_21_1.204/Light_ON_OFF_1.256 | LY01 | ON/OFF of the light | Light | Boolean
R.1.256 | /TM023_3_21_1.204/Light_level_1.256 | LN01 | Light level setpoint | Light | %
R.1.256 | /TM023_3_21_1.204/PIR_activity_1.256 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.256 | /TM023_3_21_1.204/Room_temperature_1.256 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.256 | /TM023_3_21_1.204/CO2_level_1.256 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.256 | /TM023_3_21_1.204/Window_position_1.256 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/CO2_setpoint_1.256 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Light_off_switch_high_lux_1.256 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Lux_level_ceiling_1.256 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Lux_level_setpoint_1.256 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Manual_light_on_off_switch_1.256 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Light_automatic_off_delay_1.256 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Ventilation_off_delay_1.256 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.256 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Heating_valve_1.256 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Temperature_offset_from_global_1.256 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Temperature_cooling_setpoint_1.256 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Temperature_heating_setpoint_1.256 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.256 | /TM023_3_21_1.204/Lon/Net/Rum 1.256/Temperature_global_setpoint_1.256 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.257 | /TM023_3_21_1.204/Damper_position_1.257 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.257 | /TM023_3_21_1.204/Lux_meter_1.257 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.257 | /TM023_3_21_1.204/Light_ON_OFF_1.257 | LY01 | ON/OFF of the light | Light | Boolean
R.1.257 | /TM023_3_21_1.204/Light_level_1.257 | LN01 | Light level setpoint | Light | %
R.1.257 | /TM023_3_21_1.204/PIR_activity_1.257 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.257 | /TM023_3_21_1.204/Room_temperature_1.257 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.257 | /TM023_3_21_1.204/CO2_level_1.257 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.257 | /TM023_3_21_1.204/Window_position_1.257 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/CO2_setpoint_1.257 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Light_off_switch_high_lux_1.257 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Lux_level_ceiling_1.257 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Lux_level_setpoint_1.257 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Manual_light_on_off_switch_1.257 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Light_automatic_off_delay_1.257 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Ventilation_off_delay_1.257 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.257 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Heating_valve_1.257 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Temperature_offset_from_global_1.257 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Temperature_cooling_setpoint_1.257 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Temperature_heating_setpoint_1.257 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.257 | /TM023_3_21_1.204/Lon/Net/Rum 1.257/Temperature_global_setpoint_1.257 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.258 | /TM023_3_21_1.204/Damper_position_1.258 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.258 | /TM023_3_21_1.204/Lux_meter_1.258 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.258 | /TM023_3_21_1.204/Light_ON_OFF_1.258 | LY01 | ON/OFF of the light | Light | Boolean
R.1.258 | /TM023_3_21_1.204/Light_level_1.258 | LN01 | Light level setpoint | Light | %
R.1.258 | /TM023_3_21_1.204/PIR_activity_1.258 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.258 | /TM023_3_21_1.204/Room_temperature_1.258 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.258 | /TM023_3_21_1.204/CO2_level_1.258 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.258 | /TM023_3_21_1.204/Window_position_1.258 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/CO2_setpoint_1.258 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Light_off_switch_high_lux_1.258 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Lux_level_ceiling_1.258 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Lux_level_setpoint_1.258 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Manual_light_on_off_switch_1.258 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Light_automatic_off_delay_1.258 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Ventilation_off_delay_1.258 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.258 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Heating_valve_1.258 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Temperature_offset_from_global_1.258 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Temperature_cooling_setpoint_1.258 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Temperature_heating_setpoint_1.258 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.258 | /TM023_3_21_1.204/Lon/Net/Rum 1.258/Temperature_global_setpoint_1.258 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.260 | /TM023_3_21_1.204/Damper_position_1.260 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.260 | /TM023_3_21_1.204/Lux_meter_1.260 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.260 | /TM023_3_21_1.204/Light_ON_OFF_1.260 | LY01 | ON/OFF of the light | Light | Boolean
R.1.260 | /TM023_3_21_1.204/Light_level_1.260 | LN01 | Light level setpoint | Light | %
R.1.260 | /TM023_3_21_1.204/PIR_activity_1.260 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.260 | /TM023_3_21_1.204/Room_temperature_1.260 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.260 | /TM023_3_21_1.204/CO2_level_1.260 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.260 | /TM023_3_21_1.204/Window_position_1.260 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/CO2_setpoint_1.260 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Light_off_switch_high_lux_1.260 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Lux_level_ceiling_1.260 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Lux_level_setpoint_1.260 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Manual_light_on_off_switch_1.260 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Light_automatic_off_delay_1.260 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Ventilation_off_delay_1.260 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.260 | /TM023_3_21_1.204/Signaloverførelse/Ventilation_AHU_status_1.248 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Heating_valve_1.260 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Temperature_offset_from_global_1.260 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Temperature_cooling_setpoint_1.260 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Temperature_heating_setpoint_1.260 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.260 | /TM023_3_21_1.204/Lon/Net/Rum 1.260/Temperature_global_setpoint_1.260 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.263 | /TM023_3_21_1.204/Damper_position_1.263 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.263 | /TM023_3_21_1.204/Lux_meter_1.263 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.263 | /TM023_3_21_1.204/Light_ON_OFF_1.263 | LY01 | ON/OFF of the light | Light | Boolean
R.1.263 | /TM023_3_21_1.204/Light_level_1.263 | LN01 | Light level setpoint | Light | %
R.1.263 | /TM023_3_21_1.204/PIR_activity_1.263 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.263 | /TM023_3_21_1.204/Room_temperature_1.263 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.263 | /TM023_3_21_1.204/CO2_level_1.263 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/CO2_setpoint_1.263 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Light_off_switch_high_lux_1.263 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/PIR_1.263 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Lux_level_setpoint_1.263 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Manual_light_on_off_switch_1.263 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Light_automatic_off_delay_1.263 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Ventilation_off_delay_1.263 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Ventilation_AHU_status_1.263 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Heating_valve_1.263 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Temperature_offset_from_global_1.263 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Temperature_cooling_setpoint_1.263 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Temperature_heating_setpoint_1.263 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.263 | /TM023_3_21_1.204/Lon/Net/Rum 1.263/Temperature_global_setpoint_1.263 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Damper_VAV | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Light_sensor | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Light_on_off | LY01 | ON/OFF of the light | Light | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Light_level_room | LN01 | Light level setpoint | Light | %
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Motor_valve_heating | TA01 | Opening signal of the radiator valve | Heating | %
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Heating_setpoint | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Cooling_setpoint | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Offset_STR | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp_day_deadband | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp_deadband_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Room_temp_deadband_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Runtime_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/CO2_setpoint | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Lux_level_setpoint | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Runtime_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.340 | /TM023_4_22_1.-103C/PIR_activity_1.340 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.340 | /TM023_4_22_1.-103C/Window_position_1.340 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Light_off_switch_high_lux_1.340 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Manual_light_on_off_switch_1.340 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lux_meter_1.340 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.340 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.340/Ventilation_AHU_status_1.340 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Damper_VAV | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Light_sensor | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Light_on_off | LY01 | ON/OFF of the light | Light | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Light_level_room | LN01 | Light level setpoint | Light | %
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Motor_valve_heating | TA01 | Opening signal of the radiator valve | Heating | %
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Heating_setpoint | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Cooling_setpoint | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Offset_STR | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp_day_deadband | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp_deadband_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Room_temp_deadband_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Runtime_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/CO2_setpoint | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Lux_level_setpoint | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Runtime_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.342 | /TM023_4_22_1.-103C/PIR_activity_1.342 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.342 | /TM023_4_22_1.-103C/Window_position_1.342 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lux_meter_1.342 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Light_off_switch_high_lux_1.342 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Manual_light_on_off_switch_1.342 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.342 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.342/Ventilation_AHU_status_1.342 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.344 | /TM023_4_22_1.-103C/Light_ON_OFF_1.344 | LY01 | ON/OFF of the light | Light | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Activity_in_the_room | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/CO2_set-point | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Cooling_set-point | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Heating_radiator_valve | TA01 | Opening signal of the radiator valve | Heating | %
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Heating_set-point | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_delayed_stop | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_level | LN01 | Light level setpoint | Light | %
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_level_in_the_ceiling | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_level_set-point | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_off_switch | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Light_roompanel | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature_global_deadzone_day | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature_global_deadzone_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature_global_deadzone_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Room_temperature_globel_set-point | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Temperature_offset_from_STR_panel | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Ventilation_damper_position | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Ventilation_delayed_stop_ | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Ventilation_status | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.344 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.344/Window_status | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.344 | /TM023_4_22_1.-103C/Lux_meter_1.344 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Damper_VAV | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Light_sensor | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Light_on_off | LY01 | ON/OFF of the light | Light | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Light_level_room | LN01 | Light level setpoint | Light | %
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Motor_valve_heating | TA01 | Opening signal of the radiator valve | Heating | %
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Heating_setpoint | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Cooling_setpoint | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Offset_STR | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp_day_deadband | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp_deadband_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Room_temp_deadband_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Runtime_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/CO2_setpoint | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Lux_level_setpoint | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Runtime_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.346 | /TM023_4_22_1.-103C/PIR_activity_1.346 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.346 | /TM023_4_22_1.-103C/Window_position_1.346 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lux_meter_1.346 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Light_off_switch_high_lux_1.346 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Manual_light_on_off_switch_1.346 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.346 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.346/Ventilation_AHU_status_1.346 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.348 | /TM023_4_22_1.-103C/Damper_inlet_vav | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.348 | /TM023_4_22_1.-103C/Light_sensor | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.348 | /TM023_4_22_1.-103C/Light_on_off | LY01 | ON/OFF of the light | Light | Boolean
R.1.348 | /TM023_4_22_1.-103C/Light_level_room | LN01 | Light level setpoint | Light | %
R.1.348 | /TM023_4_22_1.-103C/Motor_valve_heating | TA01 | Opening signal of the radiator valve | Heating | %
R.1.348 | /TM023_4_22_1.-103C/Room_temp | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/CO2_level | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.348 | /TM023_4_22_1.-103C/Heating_setpoint | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Cooling_setpoint | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Offset_STR | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Room_temp_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Room_temp_day_deadband | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Room_temp_deadband_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Room_temp_deadband_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.348 | /TM023_4_22_1.-103C/Runtime_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.348 | /TM023_4_22_1.-103C/CO2_setpoint | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.348 | /TM023_4_22_1.-103C/Lux_level_setpoint | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.348 | /TM023_4_22_1.-103C/Runtime_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.348 | /TM023_4_22_1.-103C/PIR_activity_1.348 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.348 | /TM023_4_22_1.-103C/Window_position_1.348 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.348 | /TM023_4_22_1.-103C/Lux_meter_1.348 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.348 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.348/Light_off_switch_high_lux_1.348 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.348 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.348/Manual_light_on_off_switch_1.348 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.348 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.348/Ventilation_AHU_status_1.348 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.350 | /TM023_4_22_1.-103C/Damper_position_1.350 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.350 | /TM023_4_22_1.-103C/Lux_meter_1.350 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.350 | /TM023_4_22_1.-103C/Light_ON_OFF_1.350 | LY01 | ON/OFF of the light | Light | Boolean
R.1.350 | /TM023_4_22_1.-103C/Light_level_1.350 | LN01 | Light level setpoint | Light | %
R.1.350 | /TM023_4_22_1.-103C/PIR_activity_1.350 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.350 | /TM023_4_22_1.-103C/Room_temperature_1.350 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.350 | /TM023_4_22_1.-103C/CO2_level_1.350 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.350 | /TM023_4_22_1.-103C/Window_position_1.350 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/CO2_setpoint_1.350 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Light_off_switch_high_lux_1.350 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Lux_level_ceiling_1.350 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Lux_level_setpoint_1.350 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Manual_light_on_off_switch_1.350 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Light_automatic_off_delay_1.350 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Ventilation_off_delay_1.350 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Ventilation_AHU_status_1.350 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Heating_valve_1.350 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Temperature_offset_from_global_1.350 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Temperature_cooling_setpoint_1.350 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Temperature_heating_setpoint_1.350 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.350 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.350/Temperature_global_setpoint_1.350 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/Damper_position_1.352 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.352 | /TM023_4_22_1.-103C/Lux_meter_1.352 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.352 | /TM023_4_22_1.-103C/Light_ON_OFF_1.352 | LY01 | ON/OFF of the light | Light | Boolean
R.1.352 | /TM023_4_22_1.-103C/Light_level_1.352 | LN01 | Light level setpoint | Light | %
R.1.352 | /TM023_4_22_1.-103C/PIR_activity_1.352 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.352 | /TM023_4_22_1.-103C/Room_temperature_1.352 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/CO2_level_1.352 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.352 | /TM023_4_22_1.-103C/Window_position_1.352 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/CO2_setpoint_1.352 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Light_off_switch_high_lux_1.352 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Lux_level_ceiling_1.352 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Lux_level_setpoint_1.352 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Manual_light_on_off_switch_1.352 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Light_automatic_off_delay_1.352 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Ventilation_off_delay_1.352 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Ventilation_AHU_status_1.352 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Heating_valve_1.352 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Temperature_offset_from_global_1.352 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Temperature_cooling_setpoint_1.352 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Temperature_heating_setpoint_1.352 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.352 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.352/Temperature_global_setpoint_1.352 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/Damper_position_1.354 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.354 | /TM023_4_22_1.-103C/Lux_meter_1.354 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.354 | /TM023_4_22_1.-103C/Light_ON_OFF_1.354 | LY01 | ON/OFF of the light | Light | Boolean
R.1.354 | /TM023_4_22_1.-103C/Light_level_1.354 | LN01 | Light level setpoint | Light | %
R.1.354 | /TM023_4_22_1.-103C/PIR_activity_1.354 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.354 | /TM023_4_22_1.-103C/Room_temperature_1.354 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/CO2_level_1.354 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.354 | /TM023_4_22_1.-103C/Window_position_1.354 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/CO2_setpoint_1.354 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Light_off_switch_high_lux_1.354 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Lux_level_ceiling_1.354 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Lux_level_setpoint_1.354 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Manual_light_on_off_switch_1.354 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Light_automatic_off_delay_1.354 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Ventilation_off_delay_1.354 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Ventilation_AHU_status_1.354 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Heating_valve_1.354 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Temperature_offset_from_global_1.354 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Temperature_cooling_setpoint_1.354 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Temperature_heating_setpoint_1.354 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.354 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.354/Temperature_global_setpoint_1.354 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/Damper_position_1.359 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.359 | /TM023_4_22_1.-103C/Lux_meter_1.359 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.359 | /TM023_4_22_1.-103C/Light_ON_OFF_1.359 | LY01 | ON/OFF of the light | Light | Boolean
R.1.359 | /TM023_4_22_1.-103C/Light_level_1.359 | LN01 | Light level setpoint | Light | %
R.1.359 | /TM023_4_22_1.-103C/PIR_activity_1.359 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.359 | /TM023_4_22_1.-103C/Room_temperature_1.359 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/CO2_level_1.359 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/CO2_setpoint_1.359 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Light_off_switch_high_lux_1.359 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Lux_level_ceiling_1.359 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Lux_level_setpoint_1.359 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Manual_light_on_off_switch_1.359 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Light_automatic_off_delay_1.359 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Ventilation_off_delay_1.359 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Heating_valve_1.359 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Temperature_offset_from_global_1.359 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Temperature_cooling_setpoint_1.359 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Temperature_heating_setpoint_1.359 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.359 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.359/Temperature_global_setpoint_1.359 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/Damper_position_1.361 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.361 | /TM023_4_22_1.-103C/Lux_meter_1.361 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.361 | /TM023_4_22_1.-103C/Light_ON_OFF_1.361 | LY01 | ON/OFF of the light | Light | Boolean
R.1.361 | /TM023_4_22_1.-103C/Light_level_1.361 | LN01 | Light level setpoint | Light | %
R.1.361 | /TM023_4_22_1.-103C/PIR_activity_1.361 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.361 | /TM023_4_22_1.-103C/Room_temperature_1.361 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/CO2_level_1.361 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.361 | /TM023_4_22_1.-103C/Window_position_1.361 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/CO2_setpoint_1.361 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Light_off_switch_high_lux_1.361 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Lux_level_ceiling_1.361 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Lux_level_setpoint_1.361 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Manual_light_on_off_switch_1.361 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Light_automatic_off_delay_1.361 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Ventilation_off_delay_1.361 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Ventilation_AHU_status_1.361 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Heating_valve_1.361 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Temperature_offset_from_global_1.361 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Temperature_cooling_setpoint_1.361 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Temperature_heating_setpoint_1.361 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.361 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.361/Temperature_global_setpoint_1.361 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/Damper_position_1.363 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.363 | /TM023_4_22_1.-103C/Lux_meter_1.363 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.363 | /TM023_4_22_1.-103C/Light_ON_OFF_1.363 | LY01 | ON/OFF of the light | Light | Boolean
R.1.363 | /TM023_4_22_1.-103C/Light_level_1.363 | LN01 | Light level setpoint | Light | %
R.1.363 | /TM023_4_22_1.-103C/PIR_activity_1.363 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.363 | /TM023_4_22_1.-103C/Room_temperature_1.363 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/CO2_level_1.363 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.363 | /TM023_4_22_1.-103C/Window_position_1.363 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/CO2_setpoint_1.363 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Light_off_switch_high_lux_1.363 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Lux_level_ceiling_1.363 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Lux_level_setpoint_1.363 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Manual_light_on_off_switch_1.363 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Light_automatic_off_delay_1.363 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Ventilation_off_delay_1.363 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Ventilation_AHU_status_1.363 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Heating_valve_1.363 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Temperature_offset_from_global_1.363 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Temperature_cooling_setpoint_1.363 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Temperature_heating_setpoint_1.363 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.363 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.363/Temperature_global_setpoint_1.363 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/Damper_position_1.365 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.365 | /TM023_4_22_1.-103C/Lux_meter_1.365 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.365 | /TM023_4_22_1.-103C/Light_ON_OFF_1.365 | LY01 | ON/OFF of the light | Light | Boolean
R.1.365 | /TM023_4_22_1.-103C/Light_level_1.365 | LN01 | Light level setpoint | Light | %
R.1.365 | /TM023_4_22_1.-103C/PIR_activity_1.365 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.365 | /TM023_4_22_1.-103C/Room_temperature_1.365 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/CO2_level_1.365 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.365 | /TM023_4_22_1.-103C/Window_position_1.365 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/CO2_setpoint_1.365 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Light_off_switch_high_lux_1.365 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Lux_level_ceiling_1.365 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Lux_level_setpoint_1.365 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Manual_light_on_off_switch_1.365 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Light_automatic_off_delay_1.365 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Ventilation_off_delay_1.365 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Ventilation_AHU_status_1.365 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Heating_valve_1.365 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Temperature_offset_from_global_1.365 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Temperature_cooling_setpoint_1.365 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Temperature_heating_setpoint_1.365 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.365 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.365/Temperature_global_setpoint_1.365 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/Damper_position_1.367 | VAV01_02 | Position of the supply/extraction damper in VAV supplied rooms | Ventilation | %
R.1.367 | /TM023_4_22_1.-103C/Lux_meter_1.367 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
R.1.367 | /TM023_4_22_1.-103C/Light_ON_OFF_1.367 | LY01 | ON/OFF of the light | Light | Boolean
R.1.367 | /TM023_4_22_1.-103C/Light_level_1.367 | LN01 | Light level setpoint | Light | %
R.1.367 | /TM023_4_22_1.-103C/PIR_activity_1.367 | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.367 | /TM023_4_22_1.-103C/Room_temperature_1.367 | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/CO2_level_1.367 | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.367 | /TM023_4_22_1.-103C/Window_position_1.367 | VINDUE_ÅBEN | Open/closed signal from window(s) in the room (does not differentiate between how many windows are opened) | Window | Boolean
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/CO2_setpoint_1.367 | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Light_off_switch_high_lux_1.367 | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Lux_level_ceiling_1.367 | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Lux_level_setpoint_1.367 | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Manual_light_on_off_switch_1.367 | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Light_automatic_off_delay_1.367 | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Ventilation_off_delay_1.367 | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Ventilation_AHU_status_1.367 | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Heating_valve_1.367 | TA01 | Opening signal of the radiator valve | Heating | %
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Temperature_offset_from_global_1.367 | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Temperature_cooling_setpoint_1.367 | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Temperature_heating_setpoint_1.367 | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.367 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.367/Temperature_global_setpoint_1.367 | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Lon/Net/Damper_inlet | SMIU01 | ON/OFF signal for the supply/extraction damper in CAV supplied rooms | Ventilation | Boolean
R.1.401 | /TM023_4_22_1.-103C/Lux_meter | LUX01 | Light level measured in the ceiling | Light | Lux
R.1.401 | /TM023_4_22_1.-103C/Light_ON_OFF | LY01 | ON/OFF of the light | Light | Boolean
R.1.401 | /TM023_4_22_1.-103C/Light_level | LN01 | Light level setpoint | Light | %
R.1.401 | /TM023_4_22_1.-103C/Activity_PIR | ZoneAktiv | If the room is considered active | Occupancy | Boolean
R.1.401 | /TM023_4_22_1.-103C/Power_switch_light | EK10 | ON/OFF switch due to high lux level in the room measured in the ceiling | Light | Boolean
R.1.401 | /TM023_4_22_1.-103C/Room_panel_light | LYS_STR350_man | Manual ON/OFF switch for the light located in the room control panel | Light | Boolean
R.1.401 | /TM023_4_22_1.-103C/Room_temperature | TRU01 | Measured room temperature (cannot be assumed to be either air or operative temperature) | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/CO2_sensor | CO201 | Current measured CO2 level in the room | CO2 | ppm
R.1.401 | /TM023_4_22_1.-103C/Setting_heating_system | TRU01KalkVarme | Lower limit for activating heating | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Setting_cooling | TRU01KalkKøl | Upper limit for activating cooling | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Offset_str_panel | TRU01_OffSet | Offset from the global temperature setpoint (manually set by the user) | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Ventilation_system_status | VentStatus | Status of the AHU supplying the room | Ventilation | Status code
R.1.401 | /TM023_4_22_1.-103C/Motor_valve_heating_system | TA01 | Opening signal of the radiator valve | Heating | %
R.1.401 | /TM023_4_22_1.-103C/Room_temperature_day | TRU01SetVærdi | Global temperature setpoint | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Setting_room_temp_dead_band_day | TRU01DødZoneDag | Deadband during daytime | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Setting_room_temp_dead_band_standby | TRU01DødZoneStandby | Deadband during standby | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Setting_room_temp_dead_band_night | TRU01DødZoneNat | Deadband during nighttime | Temperature | °C
R.1.401 | /TM023_4_22_1.-103C/Run_time_damper | VentForsStop | Delay between the room being active and when the ventilation dampers are closed automatically | Ventilation | s
R.1.401 | /TM023_4_22_1.-103C/Setting_co2_sensor | CO201_SV | Current upper limit setpoint for the CO2 level | CO2 | ppm
R.1.401 | /TM023_4_22_1.-103C/Setting_light_level | LUX01Setpunkt | Light level setpoint for when to switch off the light | Light | Lux
R.1.401 | /TM023_4_22_1.-103C/Run_time_light | PIR01DelayOff | Delay between the room being active and when the light is turned off automatically | Occupancy | s
R.1.401 | /TM023_4_22_1.-103C/Lon/Net/Rum 1.401/PIR_1.401 | PIR01 | Measurement from the PIR sensor to determine if occupied or not | Occupancy | Boolean
1
2
3
4
5
6
7
8
9
10
11
12
12
13
14
15
16
17
18
19
20
21
22
23
24

## Heating systems
Name | Name in JSON file for the SATO platform | Name in BMS system | Variable description | Unit | Number in picture
VA02 | /TM023_0_20_1128/VA02/Control_valve | MVV01_S | Signal for the control valve on the district heating return string | % | 1
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Effect | power_f (energymeter) | Current effect of the district heating supplied to the heating circuit | W | 2
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Energy_Accumulated | elec_whr_f (energymeter) | Accumulated energy use for the district heating | Wh | 3
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Flow | flow_f (energymeter) | Flow of the distrct heating (does not account for the recirculation flow) | l/s | 4
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Operation_hours_accumulated | count_f (energymeter) | Accumulated hours in operation for the heating system | h | 5
VA02 | /TM023_0_20_1128/VA02/Pump_on-off | PV01_K | ON / OFF signal for the circulation pump | Boolean | 6
VA02 | /TM023_0_20_1128/VA02/Pump_start_at_external_temperature_below | PV01_SV_VINTER_TUD01 (settings) | Activate heating system for winter conditions | °C | 7
VA02 | /TM023_0_20_1128/VA02/Pump_stop_at_external_temperature_above | TUD01_SOMMERSTOP_SV (settings) | Deactivate heating system for summer conditions | °C | 8
VA02 | /TM023_0_20_1128/VA02/Return_temperature | TR01 | Return temperature in the heating circuit | °C | 9
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Return_temperature_DH | temp_p (energymeter) | District heating return temperature | °C | 10
VA02 | /TM023_0_20_1128/VA02/Return_temperature_limit_max_deduction | TR01_FRADRAG_MAX_SV (settings) | Maximum deduction for return limit | °C | 11
VA02 | /TM023_0_20_1128/VA02/Return_temperature_max_limit | TR01_SV (settings) | Max limit of the return temperature in the heating circuit | °C | 12
VA02 | /TM023_0_20_1128/VA02/Supply_temperature | TF01 | Supply temperature in the heating circuit | °C | 13
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Supply_temperature_DH | temp_p (energymeter) | District heating supply temperature | °C | 14
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_X | TF01_KURVE_DAG_X (settings) |  | °C | 15
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_X1 | TF01_KURVE_DAG_X1 (settings) |  | °C | 16
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_X2 | TF01_KURVE_DAG_X2 (settings) |  | °C | 17
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_X3 | TF01_KURVE_DAG_X3 (settings) |  | °C | 18
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_Y | TF01_KURVE_DAG (settings) | Supply temperature for the heating circuit, without offset or additions | °C | 19
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_Y1 | TF01_KURVE_DAG_Y1 (settings) |  | °C | 20
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_Y2 | TF01_KURVE_DAG_Y2 (settings) |  | °C | 21
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_day_Y3 | TF01_KURVE_DAG_Y3 (settings) |  | °C | 22
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_displacement | TF01_FORSKYD_SV (settings) | Offset for the supply temperature in the heating circuit | °C | 23
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_X | TF01_KURVE_NAT_X (settings) |  | °C | 24
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_X1 | TF01_KURVE_NAT_X1 (settings) |  | °C | 25
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_X2 | TF01_KURVE_NAT_X2 (settings) |  | °C | 26
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_X3 | TF01_KURVE_NAT_X3 (settings) |  | °C | 27
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_Y | TF01_KURVE_NAT | Temperature to lower the supply temperature with during night setback | °C | 28
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_Y1 | TF01_KURVE_NAT_Y1 (settings) |  | °C | 29
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_Y2 | TF01_KURVE_NAT_Y2 (settings) |  | °C | 30
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_curve_night-setback_Y3 | TF01_KURVE_NAT_Y3 (settings) |  | °C | 31
VA02 | /TM023_0_20_1128/VA02/Supply_temperature_set-point | TF01_KALK_SV | Setpoint for the supply temperature in the heating circuit | °C | 32
VA02 | /TM023_0_20_1128/Lon/Net/VA02_QMV01/Kamstrup_HEAT_KMP_TAC/Node Object [0]/Volume_accumulated | vol_f (energymeter) | Accumulated volume for the district heating | l | 33
1
2
3
4
5
6
7
8
9
10
11
13
14
15 - 22
32
33
23
12
24 - 31